## Rev05
No. | Device |  | Name | Description | I/O Type | IP address =192.168.100.20 Port = 502 Slave ID = 20 | Modbus Address | Data Type (16 bit Int / Boolean?) | Query Response time (sec) | Location | Qty | Remarks
Terasaki
1 | 12 | D/G#1 | Over Speed | On overspeed [806.4min-1(112%), 828 min-1(115%)] | Digital | IP address =192.168.100.20 Port = 502 Slave ID = 20 | 1 | Boolean | 0.5 | GCP#1 | 1 |  | Engine Trip
| 12 | D/G#2 | Over Speed | On overspeed [806.4min-1(112%), 828 min-1(115%)] | Digital |  | 401 | Boolean | 0.5 | GCP#2 | 1 |  | Engine Trip
| 12 | D/G#3 | Over Speed | On overspeed [806.4min-1(112%), 828 min-1(115%)] | Digital |  | 801 | Boolean | 0.5 | GCP#3 | 1 |  | Engine Trip
| 12 | D/G#4 | Over Speed | On overspeed [806.4min-1(112%), 828 min-1(115%)] | Digital |  | 1201 | Boolean | 0.5 | GCP#4 | 1 |  | Engine Trip
2 | 48T | D/G#1 | Engine Start Failure | IN CASE OF (14) KEEPING-OFF AFTER 20 Sec FROM (88V) ACTIVATION | Digital |  | 2 | Boolean | 0.5 | GCP#1 | 1
| 48T | D/G#2 | Engine Start Failure | IN CASE OF (14) KEEPING-OFF AFTER 20 Sec FROM (88V) ACTIVATION | Digital |  | 402 | Boolean | 0.5 | GCP#2 | 1
| 48T | D/G#3 | Engine Start Failure | IN CASE OF (14) KEEPING-OFF AFTER 20 Sec FROM (88V) ACTIVATION | Digital |  | 802 | Boolean | 0.5 | GCP#3 | 1
| 48T | D/G#4 | Engine Start Failure | IN CASE OF (14) KEEPING-OFF AFTER 20 Sec FROM (88V) ACTIVATION | Digital |  | 1202 | Boolean | 0.5 | GCP#4 | 1
3 | 26EX2 | D/G#1 | Turbo-charger gas outlet temp switch (2nd) | On over 430°C | Digital |  | 3 | Boolean | 0.5 | GCP#1 | 1 |  | As per "TCTO"(T/C outlet Temp), Engine Trip
| 26EX2 | D/G#2 | Turbo-charger gas outlet temp switch (2nd) | On over 430°C | Digital |  | 403 | Boolean | 0.5 | GCP#2 | 1 |  | As per "TCTO"(T/C outlet Temp), Engine Trip
| 26EX2 | D/G#3 | Turbo-charger gas outlet temp switch (2nd) | On over 430°C | Digital |  | 803 | Boolean | 0.5 | GCP#3 | 1 |  | As per "TCTO"(T/C outlet Temp), Engine Trip
| 26EX2 | D/G#4 | Turbo-charger gas outlet temp switch (2nd) | On over 430°C | Digital |  | 1203 | Boolean | 0.5 | GCP#4 | 1 |  | As per "TCTO"(T/C outlet Temp), Engine Trip
4 | MDHH | D/G#1 | Heavy fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "15" | Digital |  | 4 | Boolean | 0.5 | GCP#1 | 1
| MDHH | D/G#2 | Heavy fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "15" | Digital |  | 404 | Boolean | 0.5 | GCP#2 | 1
| MDHH | D/G#3 | Heavy fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "15" | Digital |  | 804 | Boolean | 0.5 | GCP#3 | 1
| MDHH | D/G#4 | Heavy fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "15" | Digital |  | 1204 | Boolean | 0.5 | GCP#4 | 1
5 | 63Q2 | D/G#1 | L.O press.switch for engine (2nd) | ON BELOW 0.3MPa | Digital |  | 5 | Boolean | 0.5 | GCP#1 | 1 |  | Engine Trip
| 63Q2 | D/G#2 | L.O press.switch for engine (2nd) | ON BELOW 0.3MPa | Digital |  | 405 | Boolean | 0.5 | GCP#2 | 1 |  | Engine Trip
| 63Q2 | D/G#3 | L.O press.switch for engine (2nd) | ON BELOW 0.3MPa | Digital |  | 805 | Boolean | 0.5 | GCP#3 | 1 |  | Engine Trip
| 63Q2 | D/G#4 | L.O press.switch for engine (2nd) | ON BELOW 0.3MPa | Digital |  | 1205 | Boolean | 0.5 | GCP#4 | 1 |  | Engine Trip
6 | 26WJ2 | D/G#1 | Jacket water thermal switch (2nd) | ON OVER 90°C | Digital |  | 6 | Boolean | 0.5 | GCP#1 | 1 |  | Engine Trip
| 26WJ2 | D/G#2 | Jacket water thermal switch (2nd) | ON OVER 90°C | Digital |  | 406 | Boolean | 0.5 | GCP#2 | 1 |  | Engine Trip
| 26WJ2 | D/G#3 | Jacket water thermal switch (2nd) | ON OVER 90°C | Digital |  | 806 | Boolean | 0.5 | GCP#3 | 1 |  | Engine Trip
| 26WJ2 | D/G#4 | Jacket water thermal switch (2nd) | ON OVER 90°C | Digital |  | 1206 | Boolean | 0.5 | GCP#4 | 1 |  | Engine Trip
7 | 63QT2 | D/G#1 | L.O press.switch for turbo-charger(2nd) | ON BELOW 0.20MPa | Digital |  | 7 | Boolean | 0.5 | GCP#1 | 1 |  | Engine Trip
| 63QT2 | D/G#2 | L.O press.switch for turbo-charger(2nd) | ON BELOW 0.20MPa | Digital |  | 407 | Boolean | 0.5 | GCP#2 | 1 |  | Engine Trip
| 63QT2 | D/G#3 | L.O press.switch for turbo-charger(2nd) | ON BELOW 0.20MPa | Digital |  | 807 | Boolean | 0.5 | GCP#3 | 1 |  | Engine Trip
| 63QT2 | D/G#4 | L.O press.switch for turbo-charger(2nd) | ON BELOW 0.20MPa | Digital |  | 1207 | Boolean | 0.5 | GCP#4 | 1 |  | Engine Trip
8 | 63WJ2 | D/G#1 | Jacket water press.switch (2nd) | ON BELOW 0.1MPa | Digital |  | 8 | Boolean | 0.5 | GCP#1 | 1 |  | Engine Trip
| 63WJ2 | D/G#2 | Jacket water press.switch (2nd) | ON BELOW 0.1MPa | Digital |  | 408 | Boolean | 0.5 | GCP#2 | 1 |  | Engine Trip
| 63WJ2 | D/G#3 | Jacket water press.switch (2nd) | ON BELOW 0.1MPa | Digital |  | 808 | Boolean | 0.5 | GCP#3 | 1 |  | Engine Trip
| 63WJ2 | D/G#4 | Jacket water press.switch (2nd) | ON BELOW 0.1MPa | Digital |  | 1208 | Boolean | 0.5 | GCP#4 | 1 |  | Engine Trip
9 |  | D/G#1 | DC control power supply failure |  | Digital |  | 9 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | DC control power supply failure |  | Digital |  | 409 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | DC control power supply failure |  | Digital |  | 809 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | DC control power supply failure |  | Digital |  | 1209 | Boolean | 0.5 | GCP#4 | 1
10 |  | D/G#1 | GAC Abnormal |  | Digital |  | 10 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | GAC Abnormal |  | Digital |  | 410 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | GAC Abnormal |  | Digital |  | 810 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | GAC Abnormal |  | Digital |  | 1210 | Boolean | 0.5 | GCP#4 | 1
11 | 5E | D/G#1 | Emergency stop |  | Digital |  | 11 | Boolean | 0.5 | GCP#1 | 1 |  | To consider from drums a dry contact to GCP; purpose for the client to activate stop engine/open cb remotely
| 5E | D/G#2 | Emergency stop |  | Digital |  | 411 | Boolean | 0.5 | GCP#2 | 1 |  | To consider from drums a dry contact to GCP; purpose for the client to activate stop engine/open cb remotely
| 5E | D/G#3 | Emergency stop |  | Digital |  | 811 | Boolean | 0.5 | GCP#3 | 1 |  | To consider from drums a dry contact to GCP; purpose for the client to activate stop engine/open cb remotely
| 5E | D/G#4 | Emergency stop |  | Digital |  | 1211 | Boolean | 0.5 | GCP#4 | 1 |  | To consider from drums a dry contact to GCP; purpose for the client to activate stop engine/open cb remotely
12 | 69WJ | D/G#1 | Jacket water flow relay | ON BELOW 40m³/h | Digital |  | 12 | Boolean | 0.5 | GCP#1 | 1 |  | Timer 10 Sec
| 69WJ | D/G#2 | Jacket water flow relay | ON BELOW 40m³/h | Digital |  | 412 | Boolean | 0.5 | GCP#2 | 1 |  | Timer 10 Sec
| 69WJ | D/G#3 | Jacket water flow relay | ON BELOW 40m³/h | Digital |  | 812 | Boolean | 0.5 | GCP#3 | 1 |  | Timer 10 Sec
| 69WJ | D/G#4 | Jacket water flow relay | ON BELOW 40m³/h | Digital |  | 1212 | Boolean | 0.5 | GCP#4 | 1 |  | Timer 10 Sec
13 |  | D/G#1 | Over voltage |  | Digital |  | 13 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Over voltage |  | Digital |  | 413 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Over voltage |  | Digital |  | 813 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Over voltage |  | Digital |  | 1213 | Boolean | 0.5 | GCP#4 | 1
14 |  | D/G#1 | Under voltage |  | Digital |  | 14 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Under voltage |  | Digital |  | 414 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Under voltage |  | Digital |  | 814 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Under voltage |  | Digital |  | 1214 | Boolean | 0.5 | GCP#4 | 1
15 |  | D/G#1 | Gen differential |  | Digital |  | 15 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Gen differential |  | Digital |  | 415 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Gen differential |  | Digital |  | 815 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Gen differential |  | Digital |  | 1215 | Boolean | 0.5 | GCP#4 | 1
16 |  | D/G#1 | Reverse power |  | Digital |  | 16 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Reverse power |  | Digital |  | 416 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Reverse power |  | Digital |  | 816 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Reverse power |  | Digital |  | 1216 | Boolean | 0.5 | GCP#4 | 1
17 |  | D/G#1 | Field failure |  | Digital |  | 17 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Field failure |  | Digital |  | 417 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Field failure |  | Digital |  | 817 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Field failure |  | Digital |  | 1217 | Boolean | 0.5 | GCP#4 | 1
18 | MDH | D/G#1 | Light fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "10" | Digital |  | 18 | Boolean | 0.5 | GCP#1 | 1
| MDH | D/G#2 | Light fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "10" | Digital |  | 418 | Boolean | 0.5 | GCP#2 | 1
| MDH | D/G#3 | Light fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "10" | Digital |  | 818 | Boolean | 0.5 | GCP#3 | 1
| MDH | D/G#4 | Light fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "10" | Digital |  | 1218 | Boolean | 0.5 | GCP#4 | 1
19 | MDSY | D/G#1 | Light fault of oil mist detector system failure | ON WHEN SYSTEM FAILURE OCCURS | Digital |  | 19 | Boolean | 0.5 | GCP#1 | 1
| MDSY | D/G#2 | Light fault of oil mist detector system failure | ON WHEN SYSTEM FAILURE OCCURS | Digital |  | 419 | Boolean | 0.5 | GCP#2 | 1
| MDSY | D/G#3 | Light fault of oil mist detector system failure | ON WHEN SYSTEM FAILURE OCCURS | Digital |  | 819 | Boolean | 0.5 | GCP#3 | 1
| MDSY | D/G#4 | Light fault of oil mist detector system failure | ON WHEN SYSTEM FAILURE OCCURS | Digital |  | 1219 | Boolean | 0.5 | GCP#4 | 1
20 | 63Q1 | D/G#1 | LO press.switch for engine(1st) | ON BELOW 0.35MPa | Digital |  | 20 | Boolean | 0.5 | GCP#1 | 1 |  | As per "PTLO"
| 63Q1 | D/G#2 | LO press.switch for engine(1st) | ON BELOW 0.35MPa | Digital |  | 420 | Boolean | 0.5 | GCP#2 | 1 |  | As per "PTLO"
| 63Q1 | D/G#3 | LO press.switch for engine(1st) | ON BELOW 0.35MPa | Digital |  | 820 | Boolean | 0.5 | GCP#3 | 1 |  | As per "PTLO"
| 63Q1 | D/G#4 | LO press.switch for engine(1st) | ON BELOW 0.35MPa | Digital |  | 1220 | Boolean | 0.5 | GCP#4 | 1 |  | As per "PTLO"
21 | 63QP | D/G#1 | LO press.switch for priming | ON OVER 0.03MPa | Digital |  | 21 | Boolean | 0.5 | GCP#1 | 1 |  | NO PRESS. AFTER 60-90sec. FROM PUMP START
| 63QP | D/G#2 | LO press.switch for priming | ON OVER 0.03MPa | Digital |  | 421 | Boolean | 0.5 | GCP#2 | 1 |  | NO PRESS. AFTER 60-90sec. FROM PUMP START
| 63QP | D/G#3 | LO press.switch for priming | ON OVER 0.03MPa | Digital |  | 821 | Boolean | 0.5 | GCP#3 | 1 |  | NO PRESS. AFTER 60-90sec. FROM PUMP START
| 63QP | D/G#4 | LO press.switch for priming | ON OVER 0.03MPa | Digital |  | 1221 | Boolean | 0.5 | GCP#4 | 1 |  | NO PRESS. AFTER 60-90sec. FROM PUMP START
22 | 63WC | D/G#1 | Cooler water press switch | ON BELOW 0.1MPa | Digital |  | 22 | Boolean | 0.5 | GCP#1 | 1 |  | As per "PTCW"
| 63WC | D/G#2 | Cooler water press switch | ON BELOW 0.1MPa | Digital |  | 422 | Boolean | 0.5 | GCP#2 | 1 |  | As per "PTCW"
| 63WC | D/G#3 | Cooler water press switch | ON BELOW 0.1MPa | Digital |  | 822 | Boolean | 0.5 | GCP#3 | 1 |  | As per "PTCW"
| 63WC | D/G#4 | Cooler water press switch | ON BELOW 0.1MPa | Digital |  | 1222 | Boolean | 0.5 | GCP#4 | 1 |  | As per "PTCW"
23 | 63QT1 | D/G#1 | L.O. press switch for turbo-charger (1st) | ON BELOW 0.25MPa | Digital |  | 23 | Boolean | 0.5 | GCP#1 | 1 |  | As per "PTTLO"
| 63QT1 | D/G#2 | L.O. press switch for turbo-charger (1st) | ON BELOW 0.25MPa | Digital |  | 423 | Boolean | 0.5 | GCP#2 | 1 |  | As per "PTTLO"
| 63QT1 | D/G#3 | L.O. press switch for turbo-charger (1st) | ON BELOW 0.25MPa | Digital |  | 823 | Boolean | 0.5 | GCP#3 | 1 |  | As per "PTTLO"
| 63QT1 | D/G#4 | L.O. press switch for turbo-charger (1st) | ON BELOW 0.25MPa | Digital |  | 1223 | Boolean | 0.5 | GCP#4 | 1 |  | As per "PTTLO"
24 | 26WJ1 | D/G#1 | Jacket water thermal switch (1st) | ON OVER 85°C | Digital |  | 24 | Boolean | 0.5 | GCP#1 | 1 |  | As per "TRJWO"
| 26WJ1 | D/G#2 | Jacket water thermal switch (1st) | ON OVER 85°C | Digital |  | 424 | Boolean | 0.5 | GCP#2 | 1 |  | As per "TRJWO"
| 26WJ1 | D/G#3 | Jacket water thermal switch (1st) | ON OVER 85°C | Digital |  | 824 | Boolean | 0.5 | GCP#3 | 1 |  | As per "TRJWO"
| 26WJ1 | D/G#4 | Jacket water thermal switch (1st) | ON OVER 85°C | Digital |  | 1224 | Boolean | 0.5 | GCP#4 | 1 |  | As per "TRJWO"
25 | 26WC | D/G#1 | Cooler water thermal switch | ON OVER 50°C | Digital |  | 25 | Boolean | 0.5 | GCP#1 | 1
| 26WC | D/G#2 | Cooler water thermal switch | ON OVER 50°C | Digital |  | 425 | Boolean | 0.5 | GCP#2 | 1
| 26WC | D/G#3 | Cooler water thermal switch | ON OVER 50°C | Digital |  | 825 | Boolean | 0.5 | GCP#3 | 1
| 26WC | D/G#4 | Cooler water thermal switch | ON OVER 50°C | Digital |  | 1225 | Boolean | 0.5 | GCP#4 | 1
26 | 26Q | D/G#1 | L.O. thermal switch | ON OVER 65°C | Digital |  | 26 | Boolean | 0.5 | GCP#1 | 1
| 26Q | D/G#2 | L.O. thermal switch | ON OVER 65°C | Digital |  | 426 | Boolean | 0.5 | GCP#2 | 1
| 26Q | D/G#3 | L.O. thermal switch | ON OVER 65°C | Digital |  | 826 | Boolean | 0.5 | GCP#3 | 1
| 26Q | D/G#4 | L.O. thermal switch | ON OVER 65°C | Digital |  | 1226 | Boolean | 0.5 | GCP#4 | 1
27 | 33QSL | D/G#1 | L.O. sump tank level switch | ON BELOW LOWER LIMIT | Digital |  | 27 | Boolean | 0.5 | GCP#1 | 1 |  | Timer 5 sec
| 33QSL | D/G#2 | L.O. sump tank level switch | ON BELOW LOWER LIMIT | Digital |  | 427 | Boolean | 0.5 | GCP#2 | 1 |  | Timer 5 sec
| 33QSL | D/G#3 | L.O. sump tank level switch | ON BELOW LOWER LIMIT | Digital |  | 827 | Boolean | 0.5 | GCP#3 | 1 |  | Timer 5 sec
| 33QSL | D/G#4 | L.O. sump tank level switch | ON BELOW LOWER LIMIT | Digital |  | 1227 | Boolean | 0.5 | GCP#4 | 1 |  | Timer 5 sec
28 | 63WJ1 | D/G#1 | Jacket water press switch (1st) | ON BELOW 0.15MPa | Digital |  | 28 | Boolean | 0.5 | GCP#1 | 1 |  | As per "PTJW"
| 63WJ1 | D/G#2 | Jacket water press switch (1st) | ON BELOW 0.15MPa | Digital |  | 428 | Boolean | 0.5 | GCP#2 | 1 |  | As per "PTJW"
| 63WJ1 | D/G#3 | Jacket water press switch (1st) | ON BELOW 0.15MPa | Digital |  | 828 | Boolean | 0.5 | GCP#3 | 1 |  | As per "PTJW"
| 63WJ1 | D/G#4 | Jacket water press switch (1st) | ON BELOW 0.15MPa | Digital |  | 1228 | Boolean | 0.5 | GCP#4 | 1 |  | As per "PTJW"
29 | 63QD | D/G#1 | L.O. filter differential press switch | ON OVER 0.09MPa | Digital |  | 29 | Boolean | 0.5 | GCP#1 | 1
| 63QD | D/G#2 | L.O. filter differential press switch | ON OVER 0.09MPa | Digital |  | 429 | Boolean | 0.5 | GCP#2 | 1
| 63QD | D/G#3 | L.O. filter differential press switch | ON OVER 0.09MPa | Digital |  | 829 | Boolean | 0.5 | GCP#3 | 1
| 63QD | D/G#4 | L.O. filter differential press switch | ON OVER 0.09MPa | Digital |  | 1229 | Boolean | 0.5 | GCP#4 | 1
30 | 63QTD | D/G#1 | T/C L.O filter differential press switch | ON OVER 0.06MPa | Digital |  | 12 | Boolean | 0.5 | GCP#1 | 1
| 63QTD | D/G#2 | T/C L.O filter differential press switch | ON OVER 0.06MPa | Digital |  | 412 | Boolean | 0.5 | GCP#2 | 1
| 63QTD | D/G#3 | T/C L.O filter differential press switch | ON OVER 0.06MPa | Digital |  | 812 | Boolean | 0.5 | GCP#3 | 1
| 63QTD | D/G#4 | T/C L.O filter differential press switch | ON OVER 0.06MPa | Digital |  | 1230 | Boolean | 0.5 | GCP#4 | 1
31 | 33HF | D/G#1 | F.O leak tank level switch | ON OVER UPPER LIMIT | Digital |  | 31 | Boolean | 0.5 | GCP#1 | 1 |  | Timer 5 sec
| 33HF | D/G#2 | F.O leak tank level switch | ON OVER UPPER LIMIT | Digital |  | 431 | Boolean | 0.5 | GCP#2 | 1 |  | Timer 5 sec
| 33HF | D/G#3 | F.O leak tank level switch | ON OVER UPPER LIMIT | Digital |  | 831 | Boolean | 0.5 | GCP#3 | 1 |  | Timer 5 sec
| 33HF | D/G#4 | F.O leak tank level switch | ON OVER UPPER LIMIT | Digital |  | 1231 | Boolean | 0.5 | GCP#4 | 1 |  | Timer 5 sec
32 | TCTO | D/G#1 | EXH. GAS T/C OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40001 | 16 bit Int | 0.5 | GCP#1 | 1 |  | As per "TCTO"
| TCTO | D/G#2 | EXH. GAS T/C OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40101 | 16 bit Int | 0.5 | GCP#2 | 1 |  | As per "TCTO"
| TCTO | D/G#3 | EXH. GAS T/C OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40201 | 16 bit Int | 0.5 | GCP#3 | 1 |  | As per "TCTO"
| TCTO | D/G#4 | EXH. GAS T/C OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40301 | 16 bit Int | 0.5 | GCP#4 | 1 |  | As per "TCTO"
33 | 69WC | D/G#1 | Cooler water flow relay | ON BELOW 40m³/h | Digital |  | 32 | Boolean | 0.5 | GCP#1 | 1 |  | Timer 10 sec
| 69WC | D/G#2 | Cooler water flow relay | ON BELOW 40m³/h | Digital |  | 432 | Boolean | 0.5 | GCP#2 | 1 |  | Timer 10 sec
| 69WC | D/G#3 | Cooler water flow relay | ON BELOW 40m³/h | Digital |  | 832 | Boolean | 0.5 | GCP#3 | 1 |  | Timer 10 sec
| 69WC | D/G#4 | Cooler water flow relay | ON BELOW 40m³/h | Digital |  | 1232 | Boolean | 0.5 | GCP#4 | 1 |  | Timer 10 sec
34 | 63AC |  | Air receiver press switch for engine | On: Below 2.16MPa, Off: 2.94MPa | Digital |  | 1601 | Boolean | 0.5 | GCP | 1
| 63AC |  | Air receiver press switch for engine | On: Below 2.16MPa, Off: 2.94MPa | Digital |  | 1602 | Boolean | 0.5 | GCP | 1
| 63AC |  | Air receiver press switch for engine | On: Below 2.16MPa, Off: 2.94MPa | Digital |  | 1603 | Boolean | 0.5 | GCP | 1
35 | 63AL |  | Air receiver press switch for engine | On: Below 1.77MPa | Digital |  | 1604 | Boolean | 0.5 | GCP | 1
| 63AL |  | Air receiver press switch for engine | On: Below 1.77MPa | Digital |  | 1605 | Boolean | 0.5 | GCP | 1
| 63AL |  | Air receiver press switch for engine | On: Below 1.77MPa | Digital |  | 1606 | Boolean | 0.5 | GCP | 1
36 | 33WCH | D/G#1 | Level switch for C.W. expansion tank | On: above ___L, | Digital |  | 33 | Boolean | 0.5 | GCP#1 | 1
| 33WCH | D/G#2 | Level switch for C.W. expansion tank | On: above ___L, | Digital |  | 433 | Boolean | 0.5 | GCP#2 | 1
| 33WCH | D/G#3 | Level switch for C.W. expansion tank | On: above ___L, | Digital |  | 833 | Boolean | 0.5 | GCP#3 | 1
| 33WCH | D/G#4 | Level switch for C.W. expansion tank | On: above ___L, | Digital |  | 1233 | Boolean | 0.5 | GCP#4 | 1
37 | 33WCL | D/G#1 | Level switch for C.W. expansion tank | On: below ___L, | Digital |  | 34 | Boolean | 0.5 | GCP#1 | 1
| 33WCL | D/G#2 | Level switch for C.W. expansion tank | On: below ___L, | Digital |  | 434 | Boolean | 0.5 | GCP#2 | 1
| 33WCL | D/G#3 | Level switch for C.W. expansion tank | On: below ___L, | Digital |  | 834 | Boolean | 0.5 | GCP#3 | 1
| 33WCL | D/G#4 | Level switch for C.W. expansion tank | On: below ___L, | Digital |  | 1234 | Boolean | 0.5 | GCP#4 | 1
38 | 33WJH | D/G#1 | Level switch for J.W. expansion tank | On: above ___L, | Digital |  | 35 | Boolean | 0.5 | GCP#1 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJH | D/G#2 | Level switch for J.W. expansion tank | On: above ___L, | Digital |  | 435 | Boolean | 0.5 | GCP#2 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJH | D/G#3 | Level switch for J.W. expansion tank | On: above ___L, | Digital |  | 835 | Boolean | 0.5 | GCP#3 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJH | D/G#4 | Level switch for J.W. expansion tank | On: above ___L, | Digital |  | 1235 | Boolean | 0.5 | GCP#4 | 1 |  | Sensor by Ormin, timer 5 sec
39 | 33WJL | D/G#1 | Level switch for J.W. expansion tank | On: below ___L, | Digital |  | 36 | Boolean | 0.5 | GCP#1 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJL | D/G#2 | Level switch for J.W. expansion tank | On: below ___L, | Digital |  | 436 | Boolean | 0.5 | GCP#2 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJL | D/G#3 | Level switch for J.W. expansion tank | On: below ___L, | Digital |  | 836 | Boolean | 0.5 | GCP#3 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJL | D/G#4 | Level switch for J.W. expansion tank | On: below ___L, | Digital |  | 1236 | Boolean | 0.5 | GCP#4 | 1 |  | Sensor by Ormin, timer 5 sec
40 | 33FDH | D/G#1 | Level switch for DO service tank level high | On: above ___L, | Digital |  | 37 | Boolean | 0.5 | GCP#1 | 1 |  | timer 5 sec
| 33FDH | D/G#2 | Level switch for DO service tank level high | On: above ___L, | Digital |  | 437 | Boolean | 0.5 | GCP#2 | 1 |  | timer 5 sec
| 33FDH | D/G#3 | Level switch for DO service tank level high | On: above ___L, | Digital |  | 837 | Boolean | 0.5 | GCP#3 | 1 |  | timer 5 sec
| 33FDH | D/G#4 | Level switch for DO service tank level high | On: above ___L, | Digital |  | 1237 | Boolean | 0.5 | GCP#4 | 1 |  | timer 5 sec
41 | 33FDL | D/G#1 | Level switch for DO service tank level low | On: below ___L, | Digital |  | 38 | Boolean | 0.5 | GCP#1 | 1 |  | timer 5 sec
| 33FDL | D/G#2 | Level switch for DO service tank level low | On: below ___L, | Digital |  | 438 | Boolean | 0.5 | GCP#2 | 1 |  | timer 5 sec
| 33FDL | D/G#3 | Level switch for DO service tank level low | On: below ___L, | Digital |  | 838 | Boolean | 0.5 | GCP#3 | 1 |  | timer 5 sec
| 33FDL | D/G#4 | Level switch for DO service tank level low | On: below ___L, | Digital |  | 1238 | Boolean | 0.5 | GCP#4 | 1 |  | timer 5 sec
42 | 33FDC | D/G | Level switch for DO service tank level control | On: below ___L, Off: above ____L | Digital |  | 1607 | Boolean | 0.5 | GCP | 1 |  | timer 5 sec
43 | 33SETH | D/G | Level switch for HO settling tank level high | On: above ___L, | Digital |  | 1608 | Boolean | 0.5 | GCP | 1 |  | timer 5 sec
44 | 33SETL | D/G | Level switch for HO settling tank level low | On: below ___L, | Digital |  | 1609 | Boolean | 0.5 | GCP | 1 |  | timer 5 sec
45 | 33SETC | D/G | Level switch for HO settling tank level control | On: below ___L, Off: above ____L | Digital |  | 1610 | Boolean | 0.5 | GCP | 1 |  | timer 5 sec
46 | 33SEL | D/G | Level switch for HO service tank level low | On: below ___L, | Digital |  | 1611 | Boolean | 0.5 | GCP | 1 |  | timer 5 sec
47 | 63F | D/G#1 | F.O press.switch | ON BELOW 0.15MPa | Digital |  | 39 | Boolean | 0.5 | GCP#1 | 1 |  | As per "PTFO"
| 63F | D/G#2 | F.O press.switch | ON BELOW 0.15MPa | Digital |  | 439 | Boolean | 0.5 | GCP#2 | 1 |  | As per "PTFO"
| 63F | D/G#3 | F.O press.switch | ON BELOW 0.15MPa | Digital |  | 839 | Boolean | 0.5 | GCP#3 | 1 |  | As per "PTFO"
| 63F | D/G#4 | F.O press.switch | ON BELOW 0.15MPa | Digital |  | 1239 | Boolean | 0.5 | GCP#4 | 1 |  | As per "PTFO"
48 | 33FDRC | D/G | Level switch for F.O drain tank level control | On: below ___L, Off: above ____L | Digital |  | 1612 | Boolean | 0.5 | GCP | 1
49 | 33FDRH | D/G | Level switch for F.O drain tank | On: above ___L, | Digital |  | 1613 | Boolean | 0.5 | GCP | 1
50 | 63FB | D/G | Press switch for auto back wash filter | ON OVER 0.06MPa | Digital |  | 1614 | Boolean | 0.5 | D/G | 1
51 |  | D/G#1 | Display failure |  | Digital |  | 40 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Display failure |  | Digital |  | 440 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Display failure |  | Digital |  | 840 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Display failure |  | Digital |  | 1240 | Boolean | 0.5 | GCP#4 | 1
52 |  | D/G#1 | DC100V source abnormal |  | Digital |  | 41 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | DC100V source abnormal |  | Digital |  | 441 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | DC100V source abnormal |  | Digital |  | 841 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | DC100V source abnormal |  | Digital |  | 1241 | Boolean | 0.5 | GCP#4 | 1
53 |  | D/G#1 | DC24V source abnormal |  | Digital |  | 42 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | DC24V source abnormal |  | Digital |  | 442 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | DC24V source abnormal |  | Digital |  | 842 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | DC24V source abnormal |  | Digital |  | 1242 | Boolean | 0.5 | GCP#4 | 1
54 |  | D/G#1 | Auto synchro failure |  | Digital |  | 43 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Auto synchro failure |  | Digital |  | 443 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Auto synchro failure |  | Digital |  | 843 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Auto synchro failure |  | Digital |  | 1243 | Boolean | 0.5 | GCP#4 | 1
55 |  | D/G#1 | CB non-close |  | Digital |  | 1615 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | CB non-close |  | Digital |  | 1616 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | CB non-close |  | Digital |  | 1617 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | CB non-close |  | Digital |  | 1618 | Boolean | 0.5 | GCP#4 | 1
56 | 63AS |  | Control air press.switch | ON BELOW 0.60MPa | Digital |  | 44 | Boolean | 0.5 | GCP | 1 |  | Timer 10 sec
| 63AS |  | Control air press.switch | ON BELOW 0.60MPa | Digital |  | 444 | Boolean | 0.5 | GCP | 1 |  | Timer 10 sec
| 63AS |  | Control air press.switch | ON BELOW 0.60MPa | Digital |  | 844 | Boolean | 0.5 | GCP | 1 |  | Timer 10 sec
| 63AS |  | Control air press.switch | ON BELOW 0.60MPa | Digital |  | 1244 | Boolean | 0.5 | GCP | 1 |  | Timer 10 sec
60 | 12M | D/G#1 | Over Speed (mechanical side) | ON OVER 113% (+0%, -3%) [813.6min-1(113%)] | Digital |  | 45 | Boolean | 0.5 | D/G#1 | 1
| 12M | D/G#2 | Over Speed (mechanical side) | ON OVER 113% (+0%, -3%) [813.6min-1(113%)] | Digital |  | 445 | Boolean | 0.5 | D/G#2 | 1
| 12M | D/G#3 | Over Speed (mechanical side) | ON OVER 113% (+0%, -3%) [813.6min-1(113%)] | Digital |  | 845 | Boolean | 0.5 | D/G#3 | 1
| 12M | D/G#4 | Over Speed (mechanical side) | ON OVER 113% (+0%, -3%) [813.6min-1(113%)] | Digital |  | 1245 | Boolean | 0.5 | D/G#4 | 1
61 | 26G1 | D/G#1 | Thermal switch for alternator beaing(Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | 46 | Boolean | 0.5 | GCP#1 | 1
| 26G1 | D/G#2 | Thermal switch for alternator beaing(Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | 446 | Boolean | 0.5 | GCP#2 | 1
| 26G1 | D/G#3 | Thermal switch for alternator beaing(Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | 846 | Boolean | 0.5 | GCP#3 | 1
| 26G1 | D/G#4 | Thermal switch for alternator beaing(Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | 1246 | Boolean | 0.5 | GCP#4 | 1
62 | 26G2 | D/G#1 | Thermal switch for alternator beaing (Anti-Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | 47 | Boolean | 0.5 | GCP#1 | 1
| 26G2 | D/G#2 | Thermal switch for alternator beaing (Anti-Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | 447 | Boolean | 0.5 | GCP#2 | 1
| 26G2 | D/G#3 | Thermal switch for alternator beaing (Anti-Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | 847 | Boolean | 0.5 | GCP#3 | 1
| 26G2 | D/G#4 | Thermal switch for alternator beaing (Anti-Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | 1247 | Boolean | 0.5 | GCP#4 | 1
65 | 13 | D/G#1 | RATED SPEED | ON OVER 90% [648min-1(90%)] | Digital |  | 48 | Boolean | 0.5 | GCP#1 | 1
| 13 | D/G#2 | RATED SPEED | ON OVER 90% [648min-1(90%)] | Digital |  | 448 | Boolean | 0.5 | GCP#2 | 1
| 13 | D/G#3 | RATED SPEED | ON OVER 90% [648min-1(90%)] | Digital |  | 848 | Boolean | 0.5 | GCP#3 | 1
| 13 | D/G#4 | RATED SPEED | ON OVER 90% [648min-1(90%)] | Digital |  | 1248 | Boolean | 0.5 | GCP#4 | 1
66 | 14 | D/G#1 | LOW SPEED | ON OVER 300min-1[300min-1(41.67%)] | Digital |  | 49 | Boolean | 0.5 | GCP#1 | 1
| 14 | D/G#2 | LOW SPEED | ON OVER 300min-1[300min-1(41.67%)] | Digital |  | 449 | Boolean | 0.5 | GCP#2 | 1
| 14 | D/G#3 | LOW SPEED | ON OVER 300min-1[300min-1(41.67%)] | Digital |  | 849 | Boolean | 0.5 | GCP#3 | 1
| 14 | D/G#4 | LOW SPEED | ON OVER 300min-1[300min-1(41.67%)] | Digital |  | 1249 | Boolean | 0.5 | GCP#4 | 1
67 | 88V | D/G#1 | STARTING SOLENOID VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | 50 | Boolean | 0.5 | GCP#1 | 1
| 88V | D/G#2 | STARTING SOLENOID VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | 450 | Boolean | 0.5 | GCP#2 | 1
| 88V | D/G#3 | STARTING SOLENOID VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | 850 | Boolean | 0.5 | GCP#3 | 1
| 88V | D/G#4 | STARTING SOLENOID VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | 1250 | Boolean | 0.5 | GCP#4 | 1
68 | 5V | D/G#1 | FUEL SHUT DOWN DEVICE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | 51 | Boolean | 0.5 | GCP#1 | 1
| 5V | D/G#2 | FUEL SHUT DOWN DEVICE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | 451 | Boolean | 0.5 | GCP#2 | 1
| 5V | D/G#3 | FUEL SHUT DOWN DEVICE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | 851 | Boolean | 0.5 | GCP#3 | 1
| 5V | D/G#4 | FUEL SHUT DOWN DEVICE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | 1251 | Boolean | 0.5 | GCP#4 | 1
69 | 88L | D/G#1 | FUEL CONTROL PISTON MAGNETIC VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | 52 | Boolean | 0.5 | GCP#1 | 1
| 88L | D/G#2 | FUEL CONTROL PISTON MAGNETIC VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | 452 | Boolean | 0.5 | GCP#2 | 1
| 88L | D/G#3 | FUEL CONTROL PISTON MAGNETIC VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | 852 | Boolean | 0.5 | GCP#3 | 1
| 88L | D/G#4 | FUEL CONTROL PISTON MAGNETIC VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | 1252 | Boolean | 0.5 | GCP#4 | 1
70 | 5S | D/G#1 | FUEL OIL CUT PISTON MAGNETIC VALVE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | 53 | Boolean | 0.5 | GCP#1 | 1
| 5S | D/G#2 | FUEL OIL CUT PISTON MAGNETIC VALVE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | 453 | Boolean | 0.5 | GCP#2 | 1
| 5S | D/G#3 | FUEL OIL CUT PISTON MAGNETIC VALVE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | 853 | Boolean | 0.5 | GCP#3 | 1
| 5S | D/G#4 | FUEL OIL CUT PISTON MAGNETIC VALVE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | 1253 | Boolean | 0.5 | GCP#4 | 1
71 | MDMO | D/G#1 | MONITORING OF OIL MIST LEVEL | 0-2.0mg/L_4-20mA | Analog |  | 40002 | 16 bit Int | 0.5 | GCP#1 | 1
| MDMO | D/G#2 | MONITORING OF OIL MIST LEVEL | 0-2.0mg/L_4-20mA | Analog |  | 40102 | 16 bit Int | 0.5 | GCP#2 | 1
| MDMO | D/G#3 | MONITORING OF OIL MIST LEVEL | 0-2.0mg/L_4-20mA | Analog |  | 40202 | 16 bit Int | 0.5 | GCP#3 | 1
| MDMO | D/G#4 | MONITORING OF OIL MIST LEVEL | 0-2.0mg/L_4-20mA | Analog |  | 40302 | 16 bit Int | 0.5 | GCP#4 | 1
72 | HS | D/G#1 | GOVERNOR HANDLE SWITCH | ON: ENGINE START CONDITION | Digital |  | 54 | Boolean | 0.5 | GCP#1 | 1
| HS | D/G#2 | GOVERNOR HANDLE SWITCH | ON: ENGINE START CONDITION | Digital |  | 454 | Boolean | 0.5 | GCP#2 | 1
| HS | D/G#3 | GOVERNOR HANDLE SWITCH | ON: ENGINE START CONDITION | Digital |  | 854 | Boolean | 0.5 | GCP#3 | 1
| HS | D/G#4 | GOVERNOR HANDLE SWITCH | ON: ENGINE START CONDITION | Digital |  | 1254 | Boolean | 0.5 | GCP#4 | 1
73 | 33T | D/G#1 | TURNING HANDLE POSITION SWITCH(ON AT TURNING DEVICE OUT) | ON: ENGINE START CONDITION | Digital |  | 55 | Boolean | 0.5 | GCP#1 | 1
| 33T | D/G#2 | TURNING HANDLE POSITION SWITCH(ON AT TURNING DEVICE OUT) | ON: ENGINE START CONDITION | Digital |  | 455 | Boolean | 0.5 | GCP#2 | 1
| 33T | D/G#3 | TURNING HANDLE POSITION SWITCH(ON AT TURNING DEVICE OUT) | ON: ENGINE START CONDITION | Digital |  | 855 | Boolean | 0.5 | GCP#3 | 1
| 33T | D/G#4 | TURNING HANDLE POSITION SWITCH(ON AT TURNING DEVICE OUT) | ON: ENGINE START CONDITION | Digital |  | 1255 | Boolean | 0.5 | GCP#4 | 1
74 | 1B(U) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | 40003 | 16 bit Int | 0.5 | GCP#1 | 1
| 1B(U) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | 40103 | 16 bit Int | 0.5 | GCP#2 | 1
| 1B(U) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | 40203 | 16 bit Int | 0.5 | GCP#3 | 1
| 1B(U) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | 40303 | 16 bit Int | 0.5 | GCP#4 | 1
75 | 2B(V) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | 40004 | 16 bit Int | 0.5 | GCP#1 | 1
| 2B(V) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | 40104 | 16 bit Int | 0.5 | GCP#2 | 1
| 2B(V) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | 40204 | 16 bit Int | 0.5 | GCP#3 | 1
| 2B(V) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | 40304 | 16 bit Int | 0.5 | GCP#4 | 1
76 | 3B(W) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | 40005 | 16 bit Int | 0.5 | GCP#1 | 1
| 3B(W) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | 40105 | 16 bit Int | 0.5 | GCP#2 | 1
| 3B(W) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | 40205 | 16 bit Int | 0.5 | GCP#3 | 1
| 3B(W) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | 40305 | 16 bit Int | 0.5 | GCP#4 | 1
77 | 4B(U) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#1 | 1
| 4B(U) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#2 | 1
| 4B(U) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#3 | 1
| 4B(U) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#4 | 1
78 | 5B(V) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#1 | 1
| 5B(V) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#2 | 1
| 5B(V) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#3 | 1
| 5B(V) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#4 | 1
79 | 6B(W) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#1 | 1
| 6B(W) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#2 | 1
| 6B(W) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#3 | 1
| 6B(W) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#4 | 1
80 | 38G1 | D/G#1 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | 40006 | 16 bit Int | 0.5 | GCP#1 | 1
| 38G1 | D/G#2 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | 40106 | 16 bit Int | 0.5 | GCP#2 | 1
| 38G1 | D/G#3 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | 40206 | 16 bit Int | 0.5 | GCP#3 | 1
| 38G1 | D/G#4 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | 40306 | 16 bit Int | 0.5 | GCP#4 | 1
81 | 38G2 | D/G#1 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | 40007 | 16 bit Int | 0.5 | GCP#1 | 1
| 38G2 | D/G#2 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | 40107 | 16 bit Int | 0.5 | GCP#2 | 1
| 38G2 | D/G#3 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | 40207 | 16 bit Int | 0.5 | GCP#3 | 1
| 38G2 | D/G#4 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | 40307 | 16 bit Int | 0.5 | GCP#4 | 1
82 | TC1 | D/G#1 | EXH. GAS No. 1 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40008 | 16 bit Int | 0.5 | GCP#1 | 1
| TC1 | D/G#2 | EXH. GAS No. 1 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40108 | 16 bit Int | 0.5 | GCP#2 | 1
| TC1 | D/G#3 | EXH. GAS No. 1 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40208 | 16 bit Int | 0.5 | GCP#3 | 1
| TC1 | D/G#4 | EXH. GAS No. 1 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40308 | 16 bit Int | 0.5 | GCP#4 | 1
83 | TC2 | D/G#1 | EXH. GAS No. 2 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40009 | 16 bit Int | 0.5 | GCP#1 | 1
| TC2 | D/G#2 | EXH. GAS No. 2 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40109 | 16 bit Int | 0.5 | GCP#2 | 1
| TC2 | D/G#3 | EXH. GAS No. 2 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40209 | 16 bit Int | 0.5 | GCP#3 | 1
| TC2 | D/G#4 | EXH. GAS No. 2 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40309 | 16 bit Int | 0.5 | GCP#4 | 1
84 | TC3 | D/G#1 | EXH. GAS No. 3 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40010 | 16 bit Int | 0.5 | GCP#1 | 1
| TC3 | D/G#2 | EXH. GAS No. 3 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40110 | 16 bit Int | 0.5 | GCP#2 | 1
| TC3 | D/G#3 | EXH. GAS No. 3 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40210 | 16 bit Int | 0.5 | GCP#3 | 1
| TC3 | D/G#4 | EXH. GAS No. 3 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40310 | 16 bit Int | 0.5 | GCP#4 | 1
85 | TC4 | D/G#1 | EXH. GAS No. 4 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40011 | 16 bit Int | 0.5 | GCP#1 | 1
| TC4 | D/G#2 | EXH. GAS No. 4 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40111 | 16 bit Int | 0.5 | GCP#2 | 1
| TC4 | D/G#3 | EXH. GAS No. 4 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40211 | 16 bit Int | 0.5 | GCP#3 | 1
| TC4 | D/G#4 | EXH. GAS No. 4 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40311 | 16 bit Int | 0.5 | GCP#4 | 1
86 | TC5 | D/G#1 | EXH. GAS No. 5 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40012 | 16 bit Int | 0.5 | GCP#1 | 1
| TC5 | D/G#2 | EXH. GAS No. 5 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40112 | 16 bit Int | 0.5 | GCP#2 | 1
| TC5 | D/G#3 | EXH. GAS No. 5 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40212 | 16 bit Int | 0.5 | GCP#3 | 1
| TC5 | D/G#4 | EXH. GAS No. 5 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40312 | 16 bit Int | 0.5 | GCP#4 | 1
87 | TC6 | D/G#1 | EXH. GAS No. 6 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40013 | 16 bit Int | 0.5 | GCP#1 | 1
| TC6 | D/G#2 | EXH. GAS No. 6 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40113 | 16 bit Int | 0.5 | GCP#2 | 1
| TC6 | D/G#3 | EXH. GAS No. 6 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40213 | 16 bit Int | 0.5 | GCP#3 | 1
| TC6 | D/G#4 | EXH. GAS No. 6 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40313 | 16 bit Int | 0.5 | GCP#4 | 1
88 | TCTI | D/G#1 | EXH. GAS T/C IN | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40014 | 16 bit Int | 0.5 | GCP#1 | 1
| TCTI | D/G#2 | EXH. GAS T/C IN | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40114 | 16 bit Int | 0.5 | GCP#2 | 1
| TCTI | D/G#3 | EXH. GAS T/C IN | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40214 | 16 bit Int | 0.5 | GCP#3 | 1
| TCTI | D/G#4 | EXH. GAS T/C IN | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | 40314 | 16 bit Int | 0.5 | GCP#4 | 1
89 | FOT | D/G#1 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | 1 Litre/1 pulse | Analog |  | 40051 40052 | 32 bit Int | 0.5 | GCP#1 | 1
| FOT | D/G#2 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | 1 Litre/1 pulse | Analog |  | 40151 40152 | 32 bit Int | 0.5 | GCP#2 | 1
| FOT | D/G#3 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | 1 Litre/1 pulse | Analog |  | 40251 40252 | 32 bit Int | 0.5 | GCP#3 | 1
| FOT | D/G#4 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | 1 Litre/1 pulse | Analog |  | 40351 40352 | 32 bit Int | 0.5 | GCP#4 | 1
90 | FOEI | D/G#1 | D.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | 40053 40054 | 32 bit Int | 0.5 | GCP#1 | 1
| FOEI | D/G#2 | D.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | 40153 40154 | 32 bit Int | 0.5 | GCP#2 | 1
| FOEI | D/G#3 | D.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | 40253 40254 | 32 bit Int | 0.5 | GCP#3 | 1
| FOEI | D/G#4 | D.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | 40353 40354 | 32 bit Int | 0.5 | GCP#4 | 1
91 | FOEO | D/G#1 | D.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | 40055 40056 | 32 bit Int | 0.5 | GCP#1 | 1
| FOEO | D/G#2 | D.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | 40155 40156 | 32 bit Int | 0.5 | GCP#2 | 1
| FOEO | D/G#3 | D.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | 40255 40256 | 32 bit Int | 0.5 | GCP#3 | 1
| FOEO | D/G#4 | D.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | 40355 40356 | 32 bit Int | 0.5 | GCP#4 | 1
92 | FOHT | D/G#1 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | 1 Litre/1 pulse | Analog |  | 40057 40058 | 32 bit Int | 0.5 | GCP#1 | 1
| FOHT | D/G#2 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | 1 Litre/1 pulse | Analog |  | 40157 40158 | 32 bit Int | 0.5 | GCP#2 | 1
| FOHT | D/G#3 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | 1 Litre/1 pulse | Analog |  | 40257 40258 | 32 bit Int | 0.5 | GCP#3 | 1
| FOHT | D/G#4 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | 1 Litre/1 pulse | Analog |  | 40357 40358 | 32 bit Int | 0.5 | GCP#4 | 1
93 | FOHEI | D/G#1 | H.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | 40059 40060 | 32 bit Int | 0.5 | GCP#1 | 1
| FOHEI | D/G#2 | H.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | 40159 40160 | 32 bit Int | 0.5 | GCP#2 | 1
| FOHEI | D/G#3 | H.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | 40259 40260 | 32 bit Int | 0.5 | GCP#3 | 1
| FOHEI | D/G#4 | H.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | 40359 40360 | 32 bit Int | 0.5 | GCP#4 | 1
94 | FOHEO | D/G#1 | H.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | 40061 40062 | 32 bit Int | 0.5 | GCP#1 | 1
| FOHEO | D/G#2 | H.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | 40161 40162 | 32 bit Int | 0.5 | GCP#2 | 1
| FOHEO | D/G#3 | H.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | 40261 40262 | 32 bit Int | 0.5 | GCP#3 | 1
| FOHEO | D/G#4 | H.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | 40361 40362 | 32 bit Int | 0.5 | GCP#4 | 1
95 | PTFO | D/G#1 | PRESS. SENSOR FOR FUEL OIL | 0-1.0MPa / 4-20mA | Analog |  | 40015 | 16 bit Int | 0.5 | GCP#1 | 1
| PTFO | D/G#2 | PRESS. SENSOR FOR FUEL OIL | 0-1.0MPa / 4-20mA | Analog |  | 40115 | 16 bit Int | 0.5 | GCP#2 | 1
| PTFO | D/G#3 | PRESS. SENSOR FOR FUEL OIL | 0-1.0MPa / 4-20mA | Analog |  | 40215 | 16 bit Int | 0.5 | GCP#3 | 1
| PTFO | D/G#4 | PRESS. SENSOR FOR FUEL OIL | 0-1.0MPa / 4-20mA | Analog |  | 40315 | 16 bit Int | 0.5 | GCP#4 | 1
96 | PTJW | D/G#1 | PRESS. SENSOR FOR JACKET WATER | 0-0.6MPa / 4-20mA | Analog |  | 40016 | 16 bit Int | 0.5 | GCP#1 | 1
| PTJW | D/G#2 | PRESS. SENSOR FOR JACKET WATER | 0-0.6MPa / 4-20mA | Analog |  | 40116 | 16 bit Int | 0.5 | GCP#2 | 1
| PTJW | D/G#3 | PRESS. SENSOR FOR JACKET WATER | 0-0.6MPa / 4-20mA | Analog |  | 40216 | 16 bit Int | 0.5 | GCP#3 | 1
| PTJW | D/G#4 | PRESS. SENSOR FOR JACKET WATER | 0-0.6MPa / 4-20mA | Analog |  | 40316 | 16 bit Int | 0.5 | GCP#4 | 1
97 | PTCW | D/G#1 | PRESS. SENSOR FOR COOLER WATER | 0-0.6MPa / 4-20mA | Analog |  | 40017 | 16 bit Int | 0.5 | GCP#1 | 1
| PTCW | D/G#2 | PRESS. SENSOR FOR COOLER WATER | 0-0.6MPa / 4-20mA | Analog |  | 40117 | 16 bit Int | 0.5 | GCP#2 | 1
| PTCW | D/G#3 | PRESS. SENSOR FOR COOLER WATER | 0-0.6MPa / 4-20mA | Analog |  | 40217 | 16 bit Int | 0.5 | GCP#3 | 1
| PTCW | D/G#4 | PRESS. SENSOR FOR COOLER WATER | 0-0.6MPa / 4-20mA | Analog |  | 40317 | 16 bit Int | 0.5 | GCP#4 | 1
98 | PTLO | D/G#1 | PRESS. SENSOR FOR ENGINE L.O. | 0-1.0MPa / 4-20mA | Analog |  | 40018 | 16 bit Int | 0.5 | GCP#1 | 1
| PTLO | D/G#2 | PRESS. SENSOR FOR ENGINE L.O. | 0-1.0MPa / 4-20mA | Analog |  | 40118 | 16 bit Int | 0.5 | GCP#2 | 1
| PTLO | D/G#3 | PRESS. SENSOR FOR ENGINE L.O. | 0-1.0MPa / 4-20mA | Analog |  | 40218 | 16 bit Int | 0.5 | GCP#3 | 1
| PTLO | D/G#4 | PRESS. SENSOR FOR ENGINE L.O. | 0-1.0MPa / 4-20mA | Analog |  | 40318 | 16 bit Int | 0.5 | GCP#4 | 1
99 | PTTL0 | D/G#1 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | 0-1.0MPa / 4-20mA | Analog |  | 40019 | 16 bit Int | 0.5 | GCP#1 | 1
| PTTL0 | D/G#2 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | 0-1.0MPa / 4-20mA | Analog |  | 40119 | 16 bit Int | 0.5 | GCP#2 | 1
| PTTL0 | D/G#3 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | 0-1.0MPa / 4-20mA | Analog |  | 40219 | 16 bit Int | 0.5 | GCP#3 | 1
| PTTL0 | D/G#4 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | 0-1.0MPa / 4-20mA | Analog |  | 40319 | 16 bit Int | 0.5 | GCP#4 | 1
100 | PTIA | D/G#1 | PRESS. SENSOR FOR INTAKE-AIR | 0-0.4MPa / 4-20mA | Analog |  | 40020 | 16 bit Int | 0.5 | GCP#1 | 1
| PTIA | D/G#2 | PRESS. SENSOR FOR INTAKE-AIR | 0-0.4MPa / 4-20mA | Analog |  | 40120 | 16 bit Int | 0.5 | GCP#2 | 1
| PTIA | D/G#3 | PRESS. SENSOR FOR INTAKE-AIR | 0-0.4MPa / 4-20mA | Analog |  | 40220 | 16 bit Int | 0.5 | GCP#3 | 1
| PTIA | D/G#4 | PRESS. SENSOR FOR INTAKE-AIR | 0-0.4MPa / 4-20mA | Analog |  | 40320 | 16 bit Int | 0.5 | GCP#4 | 1
101 | 26EX1 | D/G#1 | TURBO-CHARGER GAS OUTLET TEMP. SWITCH (1st) | On over 400°C | Digital |  | 56 | Boolean | 0.5 | GCP#1 | 1 |  | T/C Outlet temperature
| 26EX1 | D/G#2 | TURBO-CHARGER GAS OUTLET TEMP. SWITCH (1st) | On over 400°C | Digital |  | 456 | Boolean | 0.5 | GCP#2 | 1 |  | T/C Outlet temperature
| 26EX1 | D/G#3 | TURBO-CHARGER GAS OUTLET TEMP. SWITCH (1st) | On over 400°C | Digital |  | 856 | Boolean | 0.5 | GCP#3 | 1 |  | T/C Outlet temperature
| 26EX1 | D/G#4 | TURBO-CHARGER GAS OUTLET TEMP. SWITCH (1st) | On over 400°C | Digital |  | 1256 | Boolean | 0.5 | GCP#4 | 1 |  | T/C Outlet temperature
102 | TRJWI | D/G#1 | TEMP. SENSOR FOR JACKET WATER INLET | PT100Ω @ 0°C | Analog |  | 40021 | 16 bit Int | 0.5 | GCP#1 | 1
| TRJWI | D/G#2 | TEMP. SENSOR FOR JACKET WATER INLET | PT100Ω @ 0°C | Analog |  | 40121 | 16 bit Int | 0.5 | GCP#2 | 1
| TRJWI | D/G#3 | TEMP. SENSOR FOR JACKET WATER INLET | PT100Ω @ 0°C | Analog |  | 40221 | 16 bit Int | 0.5 | GCP#3 | 1
| TRJWI | D/G#4 | TEMP. SENSOR FOR JACKET WATER INLET | PT100Ω @ 0°C | Analog |  | 40321 | 16 bit Int | 0.5 | GCP#4 | 1
103 | TRJWO | D/G#1 | TEMP. SENSOR FOR JACKET WATER OUTLET | PT100Ω @ 0°C | Analog |  | 40022 | 16 bit Int | 0.5 | GCP#1 | 1
| TRJWO | D/G#2 | TEMP. SENSOR FOR JACKET WATER OUTLET | PT100Ω @ 0°C | Analog |  | 40122 | 16 bit Int | 0.5 | GCP#2 | 1
| TRJWO | D/G#3 | TEMP. SENSOR FOR JACKET WATER OUTLET | PT100Ω @ 0°C | Analog |  | 40222 | 16 bit Int | 0.5 | GCP#3 | 1
| TRJWO | D/G#4 | TEMP. SENSOR FOR JACKET WATER OUTLET | PT100Ω @ 0°C | Analog |  | 40322 | 16 bit Int | 0.5 | GCP#4 | 1
104 | TRCWI | D/G#1 | TEMP. SENSOR FOR COOLER WATER INLET | PT100Ω @ 0°C | Analog |  | 40023 | 16 bit Int | 0.5 | GCP#1 | 1
| TRCWI | D/G#2 | TEMP. SENSOR FOR COOLER WATER INLET | PT100Ω @ 0°C | Analog |  | 40123 | 16 bit Int | 0.5 | GCP#2 | 1
| TRCWI | D/G#3 | TEMP. SENSOR FOR COOLER WATER INLET | PT100Ω @ 0°C | Analog |  | 40223 | 16 bit Int | 0.5 | GCP#3 | 1
| TRCWI | D/G#4 | TEMP. SENSOR FOR COOLER WATER INLET | PT100Ω @ 0°C | Analog |  | 40323 | 16 bit Int | 0.5 | GCP#4 | 1
105 | TRCWO | D/G#1 | TEMP. SENSOR FOR COOLER WATER OUTLET | PT100Ω @ 0°C | Analog |  | 40024 | 16 bit Int | 0.5 | GCP#1 | 1
| TRCWO | D/G#2 | TEMP. SENSOR FOR COOLER WATER OUTLET | PT100Ω @ 0°C | Analog |  | 40124 | 16 bit Int | 0.5 | GCP#2 | 1
| TRCWO | D/G#3 | TEMP. SENSOR FOR COOLER WATER OUTLET | PT100Ω @ 0°C | Analog |  | 40224 | 16 bit Int | 0.5 | GCP#3 | 1
| TRCWO | D/G#4 | TEMP. SENSOR FOR COOLER WATER OUTLET | PT100Ω @ 0°C | Analog |  | 40324 | 16 bit Int | 0.5 | GCP#4 | 1
106 | TRLOI | D/G#1 | TEMP. SENSOR FOR L.O. COOLER INLET | PT100Ω @ 0°C | Analog |  | 40025 | 16 bit Int | 0.5 | GCP#1 | 1
| TRLOI | D/G#2 | TEMP. SENSOR FOR L.O. COOLER INLET | PT100Ω @ 0°C | Analog |  | 40125 | 16 bit Int | 0.5 | GCP#2 | 1
| TRLOI | D/G#3 | TEMP. SENSOR FOR L.O. COOLER INLET | PT100Ω @ 0°C | Analog |  | 40225 | 16 bit Int | 0.5 | GCP#3 | 1
| TRLOI | D/G#4 | TEMP. SENSOR FOR L.O. COOLER INLET | PT100Ω @ 0°C | Analog |  | 40325 | 16 bit Int | 0.5 | GCP#4 | 1
107 | TRLOO | D/G#1 | TEMP. SENSOR FOR L.O. COOLER OUTLET | PT100Ω @ 0°C | Analog |  | 40026 | 16 bit Int | 0.5 | GCP#1 | 1
| TRLOO | D/G#2 | TEMP. SENSOR FOR L.O. COOLER OUTLET | PT100Ω @ 0°C | Analog |  | 40126 | 16 bit Int | 0.5 | GCP#2 | 1
| TRLOO | D/G#3 | TEMP. SENSOR FOR L.O. COOLER OUTLET | PT100Ω @ 0°C | Analog |  | 40226 | 16 bit Int | 0.5 | GCP#3 | 1
| TRLOO | D/G#4 | TEMP. SENSOR FOR L.O. COOLER OUTLET | PT100Ω @ 0°C | Analog |  | 40326 | 16 bit Int | 0.5 | GCP#4 | 1
108 | TRCWB | D/G#1 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | PT100Ω @ 0°C | Analog |  | 40027 | 16 bit Int | 0.5 | GCP#1 | 1
| TRCWB | D/G#2 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | PT100Ω @ 0°C | Analog |  | 40127 | 16 bit Int | 0.5 | GCP#2 | 1
| TRCWB | D/G#3 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | PT100Ω @ 0°C | Analog |  | 40227 | 16 bit Int | 0.5 | GCP#3 | 1
| TRCWB | D/G#4 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | PT100Ω @ 0°C | Analog |  | 40327 | 16 bit Int | 0.5 | GCP#4 | 1
109 | 26F1S | D/G | Thermostat switch for line heater | On below 25oC, Off over 30oC | Digital |  | 1619 | Boolean | 0.5 | GCP | 1
110 | (26F1A) |  | Thermostat switch for line heater | On over 60℃ | Digital |  | 1620 | Boolean |  | GCP | 1
111 | PTSA |  | PRESS SENSOR FOR AIR RECEIVER | 0-5.0MPa / 4-20mA | Analog |  | 40401 | 16 bit Int | 0.5 | GCP#1 | 1
| PTSA |  | PRESS SENSOR FOR AIR RECEIVER | 0-5.0MPa / 4-20mA | Analog |  | 40402 | 16 bit Int | 0.5 | GCP#2 | 1
| PTSA |  | PRESS SENSOR FOR AIR RECEIVER | 0-5.0MPa / 4-20mA | Analog |  | 40403 | 16 bit Int | 0.5 | GCP#3 | 1
112 | 26F2S | D/G | Thermostat sensor for HO Settling tank | On below 60oC, Off over 65oC | Digital |  | 1621 | Boolean | 0.5 | GCP | 1
113 | 26F2A |  | (Thermostat sensor for HO Settling tank heater) | On: above 75oC | Digital |  | 1622 | Boolean |  | GCP | 1 |  | Overheat, heater stop operation
114 | 26F3S |  | Thermostat switch for HO Service tank heater | On below 90oC, Off over 95oC | Digital |  | 1623 | Boolean |  | GCP | 1
115 | 26F4 |  | Thermostat switch for HO Service tank(upper) | On over 90oC, Off below 85oC | Digital |  | 1624 | Boolean |  | GCP | 1
116 | 26F3A |  | (Thermostat switch for HO Service tank heater) | On: above 105oC | Digital |  | 1625 | Boolean |  | GCP | 1 |  | Overheat, heater stop operation
117 | 26F7 |  | Thermostat switch for HO Engine inlet | On below 110oC, Off over 115oC | Digital |  | 1626 | Boolean |  | GCP | 1
118 | 26F8 |  | Thermostat switch for HO Engine inlet | On below 130oC, Off below 125oC | Digital |  | 1627 | Boolean |  | GCP | 1
119 | 63FH |  | Press switch for HO piping | On below 0.5MPa | Digital |  | 1628 | Boolean |  | GCP | 1
120 | 63FD |  | Press switch for DO piping | On below 0.35MPa | Digital |  | 1629 | Boolean |  | GCP | 1
121 | LSDO | D/G#1 | Limit switch for change over valve | On D.O.side | Digital |  | 57 | Boolean | 0.5 | GCP#1 | 1
| LSDO | D/G#1 | Limit switch for change over valve | On D.O.side | Digital |  | 58 | Boolean | 0.5 | GCP#1 | 1
| LSDO | D/G#2 | Limit switch for change over valve | On D.O.side | Digital |  | 457 | Boolean | 0.5 | GCP#2 | 1
| LSDO | D/G#2 | Limit switch for change over valve | On D.O.side | Digital |  | 458 | Boolean | 0.5 | GCP#2 | 1
| LSDO | D/G#3 | Limit switch for change over valve | On D.O.side | Digital |  | 857 | Boolean | 0.5 | GCP#3 | 1
| LSDO | D/G#3 | Limit switch for change over valve | On D.O.side | Digital |  | 858 | Boolean | 0.5 | GCP#3 | 1
| LSDO | D/G#4 | Limit switch for change over valve | On D.O.side | Digital |  | 1257 | Boolean | 0.5 | GCP#4 | 1
| LSDO | D/G#4 | Limit switch for change over valve | On D.O.side | Digital |  | 1258 | Boolean | 0.5 | GCP#4 | 1
122 | LSHO | D/G#1 | Limit switch for change over valve | On H.O.side | Digital |  | 59 | Boolean | 0.5 | GCP#1 | 1
| LSHO | D/G#1 | Limit switch for change over valve | On H.O.side | Digital |  | 60 | Boolean | 0.5 | GCP#1 | 1
| LSHO | D/G#2 | Limit switch for change over valve | On H.O.side | Digital |  | 459 | Boolean | 0.5 | GCP#2 | 1
| LSHO | D/G#2 | Limit switch for change over valve | On H.O.side | Digital |  | 460 | Boolean | 0.5 | GCP#2 | 1
| LSHO | D/G#3 | Limit switch for change over valve | On H.O.side | Digital |  | 859 | Boolean | 0.5 | GCP#3 | 1
| LSHO | D/G#3 | Limit switch for change over valve | On H.O.side | Digital |  | 860 | Boolean | 0.5 | GCP#3 | 1
| LSHO | D/G#4 | Limit switch for change over valve | On H.O.side | Digital |  | 1259 | Boolean | 0.5 | GCP#4 | 1
| LSHO | D/G#4 | Limit switch for change over valve | On H.O.side | Digital |  | 1260 | Boolean | 0.5 | GCP#4 | 1
123 | 26F9S |  | Thermostat switch for Drain Tank | On below 50oC, Off below 55oC | Digital |  | 1630 | Boolean |  | GCP | 1
124 | 26F9A |  | (Thermostat switch for Drain Tank Heater) | On: above 65oC | Digital |  | 1631 | Boolean |  | GCP | 1 |  | Overheat, heater stop operation
125 | TRDI | D/G#1 | TEMP. SENSOR for DO Engine inlet | PT100Ω @ 0°C | Analog |  | 40028 | 16 bit Int | 0.5 | GCP#1 | 1
| TRDI | D/G#2 | TEMP. SENSOR for DO Engine inlet | PT100Ω @ 0°C | Analog |  | 40128 | 16 bit Int | 0.5 | GCP#2 | 1
| TRDI | D/G#3 | TEMP. SENSOR for DO Engine inlet | PT100Ω @ 0°C | Analog |  | 40228 | 16 bit Int | 0.5 | GCP#3 | 1
| TRDI | D/G#4 | TEMP. SENSOR for DO Engine inlet | PT100Ω @ 0°C | Analog |  | 40328 | 16 bit Int | 0.5 | GCP#4 | 1
126 | TRDO | D/G#1 | TEMP. SENSOR for DO Engine outlet | PT100Ω @ 0°C | Analog |  | 40029 | 16 bit Int | 0.5 | GCP#1 | 1
| TRDO | D/G#2 | TEMP. SENSOR for DO Engine outlet | PT100Ω @ 0°C | Analog |  | 40129 | 16 bit Int | 0.5 | GCP#2 | 1
| TRDO | D/G#3 | TEMP. SENSOR for DO Engine outlet | PT100Ω @ 0°C | Analog |  | 40229 | 16 bit Int | 0.5 | GCP#3 | 1
| TRDO | D/G#4 | TEMP. SENSOR for DO Engine outlet | PT100Ω @ 0°C | Analog |  | 40329 | 16 bit Int | 0.5 | GCP#4 | 1
127 | TRHI | D/G#1 | TEMP. SENSOR for HO Engine inlet | PT100Ω @ 0°C | Analog |  | 40030 | 16 bit Int | 0.5 | GCP#1 | 1
| TRHI | D/G#2 | TEMP. SENSOR for HO Engine inlet | PT100Ω @ 0°C | Analog |  | 40130 | 16 bit Int | 0.5 | GCP#2 | 1
| TRHI | D/G#3 | TEMP. SENSOR for HO Engine inlet | PT100Ω @ 0°C | Analog |  | 40230 | 16 bit Int | 0.5 | GCP#3 | 1
| TRHI | D/G#4 | TEMP. SENSOR for HO Engine inlet | PT100Ω @ 0°C | Analog |  | 40330 | 16 bit Int | 0.5 | GCP#4 | 1
128 | TRHO | D/G#1 | TEMP. SENSOR for HO Engine outlet | PT100Ω @ 0°C | Analog |  | 40031 | 16 bit Int | 0.5 | GCP#1 | 1
| TRHO | D/G#2 | TEMP. SENSOR for HO Engine outlet | PT100Ω @ 0°C | Analog |  | 40131 | 16 bit Int | 0.5 | GCP#2 | 1
| TRHO | D/G#3 | TEMP. SENSOR for HO Engine outlet | PT100Ω @ 0°C | Analog |  | 40231 | 16 bit Int | 0.5 | GCP#3 | 1
| TRHO | D/G#4 | TEMP. SENSOR for HO Engine outlet | PT100Ω @ 0°C | Analog |  | 40331 | 16 bit Int | 0.5 | GCP#4 | 1
129 |  |  | Viscosity controller | less than 230 CST | Digital |  | 1632 | Boolean | 0.5 |  | 1
130 | TRRA1 | D/G#1 | TEMP. SENSOR FOR RADIATOR 1 | Fault | Digital |  | 40040 | Boolean | 0.5 | D/G#1 | 1
| TRRA1 | D/G#2 | TEMP. SENSOR FOR RADIATOR 1 | Fault | Digital |  | 40140 | Boolean | 0.5 | D/G#2 | 1
| TRRA1 | D/G#3 | TEMP. SENSOR FOR RADIATOR 1 | Fault | Digital |  | 40240 | Boolean | 0.5 | D/G#3 | 1
| TRRA1 | D/G#4 | TEMP. SENSOR FOR RADIATOR 1 | Fault | Digital |  | 40340 | Boolean | 0.5 | D/G#4 | 1
131 | TRRA2 | D/G#1 | TEMP. SENSOR FOR RADIATOR 2 | Fault | Digital |  | 40041 | Boolean | 0.5 | D/G#1 | 1
| TRRA2 | D/G#2 | TEMP. SENSOR FOR RADIATOR 2 | Fault | Digital |  | 40141 | Boolean | 0.5 | D/G#2 | 1
| TRRA2 | D/G#3 | TEMP. SENSOR FOR RADIATOR 2 | Fault | Digital |  | 40241 | Boolean | 0.5 | D/G#3 | 1
| TRRA2 | D/G#4 | TEMP. SENSOR FOR RADIATOR 2 | Fault | Digital |  | 40341 | Boolean | 0.5 | D/G#4 | 1
132 | TRRA3 | D/G#1 | TEMP. SENSOR FOR RADIATOR 3 | Fault | Digital |  | 40042 | Boolean | 0.5 | D/G#1 | 1
| TRRA3 | D/G#2 | TEMP. SENSOR FOR RADIATOR 3 | Fault | Digital |  | 40142 | Boolean | 0.5 | D/G#2 | 1
| TRRA3 | D/G#3 | TEMP. SENSOR FOR RADIATOR 3 | Fault | Digital |  | 40242 | Boolean | 0.5 | D/G#3 | 1
| TRRA3 | D/G#4 | TEMP. SENSOR FOR RADIATOR 3 | Fault | Digital |  | 40342 | Boolean | 0.5 | D/G#4 | 1
133 | TRRA4 | D/G#1 | TEMP. SENSOR FOR RADIATOR 4 | Fault | Digital |  | 40043 | Boolean | 0.5 | D/G#1 | 1
| TRRA4 | D/G#2 | TEMP. SENSOR FOR RADIATOR 4 | Fault | Digital |  | 40143 | Boolean | 0.5 | D/G#2 | 1
| TRRA4 | D/G#3 | TEMP. SENSOR FOR RADIATOR 4 | Fault | Digital |  | 40243 | Boolean | 0.5 | D/G#3 | 1
| TRRA4 | D/G#4 | TEMP. SENSOR FOR RADIATOR 4 | Fault | Digital |  | 40343 | Boolean | 0.5 | D/G#4 | 1
134 | HOPF |  | H.O. Purifier Abnormal |  | Digital |  | 1633 | Boolean | 0.5 | GCP | 1
135 | LOPF |  | Lub.Oil Purifier Abnormal |  | Digital |  | 1634 | Boolean | 0.5 | GCP | 1
136 | MD-SX | D/G#1 | OMD ANALOG OUTPUT BOARD |  | Analog |  | 40032 | 16 bit Int | 0.5 | D/G#1 | 1
| MD-SX | D/G#2 | OMD ANALOG OUTPUT BOARD |  | Analog |  | 40132 | 16 bit Int | 0.5 | D/G#2 | 1
| MD-SX | D/G#3 | OMD ANALOG OUTPUT BOARD |  | Analog |  | 40232 | 16 bit Int | 0.5 | D/G#3 | 1
| MD-SX | D/G#4 | OMD ANALOG OUTPUT BOARD |  | Analog |  | 40332 | 16 bit Int | 0.5 | D/G#4 | 1
137 | 33SD |  | Level Switch for Sludge Tank |  | Digital |  | 1635 | Boolean |  | GCP | 1
140 |  | D/G#1 | Voltage [Generator] | V | Analog |  | 40033 | 16 bit Int | 0.5 | GCP#1 | 1
|  | D/G#2 | Voltage [Generator] | V | Analog |  | 40133 | 16 bit Int | 0.5 | GCP#2 | 1
|  | D/G#3 | Voltage [Generator] | V | Analog |  | 40233 | 16 bit Int | 0.5 | GCP#3 | 1
|  | D/G#4 | Voltage [Generator] | V | Analog |  | 40333 | 16 bit Int | 0.5 | GCP#4 | 1
141 |  | D/G#1 | Frequency [Generator] | Hz | Analog |  | 40034 | 16 bit Int | 0.5 | GCP#1 | 1
|  | D/G#2 | Frequency [Generator] | Hz | Analog |  | 40134 | 16 bit Int | 0.5 | GCP#2 | 1
|  | D/G#3 | Frequency [Generator] | Hz | Analog |  | 40234 | 16 bit Int | 0.5 | GCP#3 | 1
|  | D/G#4 | Frequency [Generator] | Hz | Analog |  | 40334 | 16 bit Int | 0.5 | GCP#4 | 1
141A |  | D/G#1 | Power Factor [Generator] |  | Analog |  | 40035 | 16 bit Int | 0.5 | GCP#1 | 1
|  | D/G#2 | Power Factor [Generator] |  | Analog |  | 40135 | 16 bit Int | 0.5 | GCP#2 | 1
|  | D/G#3 | Power Factor [Generator] |  | Analog |  | 40235 | 16 bit Int | 0.5 | GCP#3 | 1
|  | D/G#4 | Power Factor [Generator] |  | Analog |  | 40335 | 16 bit Int | 0.5 | GCP#4 | 1
142 | 52G1 |  | VCB Status [Generator][52G1] | Close | Digital |  | 65 | Boolean | 0.5 | GCP#1 | 1
|  |  |  | Open | Digital |  | 66 | Boolean | 0.5 | GCP#1 | 1
|  |  |  | Fault (Non-close)/trip | Digital |  | 67 | Boolean | 0.5 | GCP#1 | 1
| 52G2 |  | VCB Status [Generator][52G1] | Close | Digital |  | 465 | Boolean | 0.5 | GCP#2 | 1
|  |  |  | Open | Digital |  | 466 | Boolean | 0.5 | GCP#2 | 1
|  |  |  | Fault (Non-close)/trip | Digital |  | 467 | Boolean | 0.5 | GCP#2 | 1
| 52G3 |  | VCB Status [Generator][52G1] | Close | Digital |  | 865 | Boolean | 0.5 | GCP#3 | 1
|  |  |  | Open | Digital |  | 866 | Boolean | 0.5 | GCP#3 | 1
|  |  |  | Fault (Non-close)/trip | Digital |  | 867 | Boolean | 0.5 | GCP#3 | 1
| 52G4 |  | VCB Status [Generator][52G1] | Close | Digital |  | 1265 | Boolean | 0.5 | GCP#4 | 1
|  |  |  | Open | Digital |  | 1266 | Boolean | 0.5 | GCP#4 | 1
|  |  |  | Fault (Non-close)/trip | Digital |  | 1267 | Boolean | 0.5 | GCP#4 | 1
143 |  | D/G#1 | Current [Generator] | Amphere | Analog |  | 40036 | 16 bit Int | 0.5 | GCP#1 | 1
|  | D/G#2 | Current [Generator] | Amphere | Analog |  | 40136 | 16 bit Int | 0.5 | GCP#2 | 1
|  | D/G#3 | Current [Generator] | Amphere | Analog |  | 40236 | 16 bit Int | 0.5 | GCP#3 | 1
|  | D/G#4 | Current [Generator] | Amphere | Analog |  | 40336 | 16 bit Int | 0.5 | GCP#4 | 1
144 |  | D/G#1 | Running hours [Generator] | hrs | Analog |  | 40063 40064 | 32 bit Int | 0.5 | GCP#1 | 1
|  | D/G#2 | Running hours [Generator] | hrs | Analog |  | 40163 40164 | 32 bit Int | 0.5 | GCP#2 | 1
|  | D/G#3 | Running hours [Generator] | hrs | Analog |  | 40263 40264 | 32 bit Int | 0.5 | GCP#3 | 1
|  | D/G#4 | Running hours [Generator] | hrs | Analog |  | 40363 40364 | 32 bit Int | 0.5 | GCP#4 | 1
145 |  | D/G#1 | Rack Reading | mm | Analog |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Rack Reading | mm | Analog |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Rack Reading | mm | Analog |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Rack Reading | mm | Analog |  |  |  | 0.5 | GCP#4 | 1
146 |  | D/G#1 | Power [Generator] | kWe | Analog |  | 40038 | 16 bit Int | 0.5 | GCP#1 | 1
|  | D/G#2 | Power [Generator] | kWe | Analog |  | 40138 | 16 bit Int | 0.5 | GCP#2 | 1
|  | D/G#3 | Power [Generator] | kWe | Analog |  | 40238 | 16 bit Int | 0.5 | GCP#3 | 1
|  | D/G#4 | Power [Generator] | kWe | Analog |  | 40338 | 16 bit Int | 0.5 | GCP#4 | 1
147 |  | D/G#1 | Engine RPM | min-1 | Analog |  | 40039 | 16 bit Int | 0.5 | GCP#1 | 1
|  | D/G#2 | Engine RPM | min-1 | Analog |  | 40139 | 16 bit Int | 0.5 | GCP#2 | 1
|  | D/G#3 | Engine RPM | min-1 | Analog |  | 40239 | 16 bit Int | 0.5 | GCP#3 | 1
|  | D/G#4 | Engine RPM | min-1 | Analog |  | 40339 | 16 bit Int | 0.5 | GCP#4 | 1
154 |  | D/G#1 | Ready to start |  | Digital |  | 68 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Ready to start |  | Digital |  | 468 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Ready to start |  | Digital |  | 868 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Ready to start |  | Digital |  | 1268 | Boolean | 0.5 | GCP#4 | 1
155 | IM1 |  | No.1 Turning Motor | Abnormal trip | Digital |  | 69 | Boolean |  | GCP#1 | 1
|  |  |  | FWD Running | Digital |  | 70 | Boolean |  | GCP#1 | 1
|  |  |  | Rev Running | Digital |  | 71 | Boolean |  | GCP#1 | 1
|  |  |  | Remote mode | Digital |  | 72 | Boolean |  | GCP#1 | 1
|  |  | No.2 Turning Motor | Abnormal trip | Digital |  | 469 | Boolean |  | GCP#2 | 1
|  |  |  | FWD Running | Digital |  | 470 | Boolean |  | GCP#2 | 1
|  |  |  | Rev Running | Digital |  | 471 | Boolean |  | GCP#2 | 1
|  |  |  | Remote mode | Digital |  | 472 | Boolean |  | GCP#2 | 1
|  |  | No.3 Turning Motor | Abnormal trip | Digital |  | 869 | Boolean |  | GCP#3 | 1
|  |  |  | FWD Running | Digital |  | 870 | Boolean |  | GCP#3 | 1
|  |  |  | Rev Running | Digital |  | 871 | Boolean |  | GCP#3 | 1
|  |  |  | Remote mode | Digital |  | 872 | Boolean |  | GCP#3 | 1
|  |  | No.4 Turning Motor | Abnormal trip | Digital |  | 1269 | Boolean |  | GCP#4 | 1
|  |  |  | FWD Running | Digital |  | 1270 | Boolean |  | GCP#4 | 1
|  |  |  | Rev Running | Digital |  | 1271 | Boolean |  | GCP#4 | 1
|  |  |  | Remote mode | Digital |  | 1272 | Boolean |  | GCP#4 | 1
156 | IM2 |  | No.1 LO Priming Pump Motor status | Auto start [GCP] | Digital |  | 73 | Boolean |  | GCP#1 | 1
|  |  |  | Auto Stop {GCP] | Digital |  | 74 | Boolean |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  | 75 | Boolean |  | GCP#1 | 1
|  |  |  | Running | Digital |  | 76 | Boolean |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  | 77 | Boolean |  | GCP#1 | 1
|  |  |  | Remote start [LCP] | Digital |  | 78 | Boolean |  | GCP#1 | 1
|  |  |  | Remote Stop [LCP] | Digital |  | 79 | Boolean |  | GCP#1 | 1
|  |  | No.2 LO Priming Pump Motor status | Auto start [GCP] | Digital |  | 473 | Boolean |  | GCP#2 | 1
|  |  |  | Auto Stop {GCP] | Digital |  | 474 | Boolean |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  | 475 | Boolean |  | GCP#2 | 1
|  |  |  | Running | Digital |  | 476 | Boolean |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  | 477 | Boolean |  | GCP#2 | 1
|  |  |  | Remote start [LCP] | Digital |  | 478 | Boolean |  | GCP#2 | 1
|  |  |  | Remote Stop [LCP] | Digital |  | 479 | Boolean |  | GCP#2 | 1
|  |  | No.3 LO Priming Pump Motor status | Auto start [GCP] | Digital |  | 873 | Boolean |  | GCP#3 | 1
|  |  |  | Auto Stop {GCP] | Digital |  | 874 | Boolean |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  | 875 | Boolean |  | GCP#3 | 1
|  |  |  | Running | Digital |  | 876 | Boolean |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  | 877 | Boolean |  | GCP#3 | 1
|  |  |  | Remote start [LCP] | Digital |  | 878 | Boolean |  | GCP#3 | 1
|  |  |  | Remote Stop [LCP] | Digital |  | 879 | Boolean |  | GCP#3 | 1
|  |  | No.4 LO Priming Pump Motor status | Auto start [GCP] | Digital |  | 1273 | Boolean |  | GCP#4 | 1
|  |  |  | Auto Stop {GCP] | Digital |  | 1274 | Boolean |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  | 1275 | Boolean |  | GCP#4 | 1
|  |  |  | Running | Digital |  | 1276 | Boolean |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  | 1277 | Boolean |  | GCP#4 | 1
|  |  |  | Remote start [LCP] | Digital |  | 1278 | Boolean |  | GCP#4 | 1
|  |  |  | Remote Stop [LCP] | Digital |  | 1279 | Boolean |  | GCP#4 | 1
157 | IM3 |  | No.1 Air Compressor status | Auto start [GCP] | Digital |  | 1636 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1637 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1638 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1639 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1616 | Boolean |  | GCP | 1
|  |  | No.2 Air Compressor status | Auto start [GCP] | Digital |  | 1617 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1642 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1616 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1644 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1645 | Boolean |  | GCP | 1
158 | IM4 |  | No.1 Mist Fan | Auto start [GCP] | Digital |  | 80 | Boolean |  | GCP#1 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 81 | Boolean |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  | 82 | Boolean |  | GCP#1 | 1
|  |  |  | Running | Digital |  | 83 | Boolean |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  | 84 | Boolean |  | GCP#1 | 1
|  |  | No.2 Mist Fan | Auto start [GCP] | Digital |  | 480 | Boolean |  | GCP#2 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 481 | Boolean |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  | 482 | Boolean |  | GCP#2 | 1
|  |  |  | Running | Digital |  | 483 | Boolean |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  | 484 | Boolean |  | GCP#2 | 1
|  |  | No.3 Mist Fan | Auto start [GCP] | Digital |  | 880 | Boolean |  | GCP#3 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 881 | Boolean |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  | 882 | Boolean |  | GCP#3 | 1
|  |  |  | Running | Digital |  | 883 | Boolean |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  | 884 | Boolean |  | GCP#3 | 1
|  |  | No.4 Mist Fan | Auto start [GCP] | Digital |  | 1280 | Boolean |  | GCP#4 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1281 | Boolean |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  | 1282 | Boolean |  | GCP#4 | 1
|  |  |  | Running | Digital |  | 1283 | Boolean |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  | 1284 | Boolean |  | GCP#4 | 1
159 | IM5 |  | No.1 DO Transfer Pump | Auto start [GCP] | Digital |  | 1646 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1647 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1648 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1649 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1650 | Boolean |  | GCP | 1
|  |  | No.2 DO Transfer Pump | Auto start [GCP] | Digital |  | 1651 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1652 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1653 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1654 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1655 | Boolean |  | GCP | 1
160 | IM6 |  | No.1 DO Feed Pump | Auto start [GCP] | Digital |  | 1656 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1657 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1658 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1659 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1660 | Boolean |  | GCP | 1
|  |  | No.2 DO Feed Pump | Auto start [GCP] | Digital |  | 1661 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1662 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1663 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1664 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1665 | Boolean |  | GCP | 1
161 | IM7 |  | No.1 HO Transfer Pump | Auto start [GCP] | Digital |  | 1666 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1667 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1668 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1669 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1670 | Boolean |  | GCP | 1
|  |  | No.2 HO Transfer Pump | Auto start [GCP] | Digital |  | 1671 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1672 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1673 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1674 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1675 | Boolean |  | GCP | 1
162 | IM8 |  | No.1 HO Pressure Pump | Auto start [GCP] | Digital |  | 1676 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1677 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1678 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1679 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1680 | Boolean |  | GCP | 1
|  |  | No.2 HO Pressure Pump | Auto start [GCP] | Digital |  | 1681 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1682 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1683 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1684 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1685 | Boolean |  | GCP | 1
163 | IM9 |  | No.1 HO Feed Pump | Auto start [GCP] | Digital |  | 1686 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1687 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1688 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1689 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1690 | Boolean |  | GCP | 1
|  |  | No.2 HO Feed Pump | Auto start [GCP] | Digital |  | 1691 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1692 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1693 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1694 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1695 | Boolean |  | GCP | 1
164 | I10 |  | No.1 FO Drain Pump | Auto start [GCP] | Digital |  | 1696 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1697 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1698 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1699 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1700 | Boolean |  | GCP | 1
|  |  | No.2 FO Drain Pump | Auto start [GCP] | Digital |  | 1701 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1702 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1703 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1704 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1705 | Boolean |  | GCP | 1
165 | IM11 |  | No.1 DO/HO change over valve [Engine inlet] | Energize | Digital |  | 85 | Boolean |  | GCP#1 | 1
|  |  |  | De-energize | Digital |  | 86 | Boolean |  | GCP#1 | 1
|  |  | No.2 DO/HO change over valve [Engine inlet] | Energize | Digital |  | 485 | Boolean |  | GCP#2 | 1
|  |  |  | De-energize | Digital |  | 486 | Boolean |  | GCP#2 | 1
|  |  | No.3 DO/HO change over valve [Engine inlet] | Energize | Digital |  | 885 | Boolean |  | GCP#3 | 1
|  |  |  | De-energize | Digital |  | 886 | Boolean |  | GCP#3 | 1
|  |  | No.4 DO/HO change over valve [Engine inlet] | Energize | Digital |  | 1285 | Boolean |  | GCP#4 | 1
|  |  |  | De-energize | Digital |  | 1286 | Boolean |  | GCP#4 | 1
|  |  | No.1 DO/HO change over valve [Engine outlet] | Energize | Digital |  | 87 | Boolean |  | GCP#1 | 1
|  |  |  | De-energize | Digital |  | 88 | Boolean |  | GCP#1 | 1
|  |  | No.2 DO/HO change over valve [Engine outlet] | Energize | Digital |  | 487 | Boolean |  | GCP#2 | 1
|  |  |  | De-energize | Digital |  | 488 | Boolean |  | GCP#2 | 1
|  |  | No.3 DO/HO change over valve [Engine outlet] | Energize | Digital |  | 887 | Boolean |  | GCP#3 | 1
|  |  |  | De-energize | Digital |  | 888 | Boolean |  | GCP#3 | 1
|  |  | No.4 DO/HO change over valve [Engine outlet] | Energize | Digital |  | 1287 | Boolean |  | GCP#4 | 1
|  |  |  | De-energize | Digital |  | 1288 | Boolean |  | GCP#4 | 1
166 | IM12 |  | No.1 Inlet Fan | Auto start [GCP] | Digital |  | 1706 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1707 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1708 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1709 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1710 | Boolean |  | GCP | 1
|  |  | No.2 Inlet Fan | Auto start [GCP] | Digital |  | 1711 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1712 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1713 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1714 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1715 | Boolean |  | GCP | 1
|  |  | No.3 Inlet Fan | Auto start [GCP] | Digital |  | 1716 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1717 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1718 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1719 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1720 | Boolean |  | GCP | 1
|  |  | No.4 Inlet Fan | Auto start [GCP] | Digital |  | 1721 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1722 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1723 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1724 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1725 | Boolean |  | GCP | 1
|  |  | No.5 Inlet Fan | Auto start [GCP] | Digital |  | 1726 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1727 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1728 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1729 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1730 | Boolean |  | GCP | 1
167 | IM13 |  | No.1 Outlet Fan | Auto start [GCP] | Digital |  | 1731 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1732 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1733 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1734 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1735 | Boolean |  | GCP | 1
|  |  | No.2 Outlet Fan | Auto start [GCP] | Digital |  | 1736 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1737 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1738 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1739 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1740 | Boolean |  | GCP | 1
|  |  | No.3 Outlet Fan | Auto start [GCP] | Digital |  | 1741 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1742 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1743 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1744 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1745 | Boolean |  | GCP | 1
|  |  | No.4 Outlet Fan | Auto start [GCP] | Digital |  | 1746 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1747 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1748 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1749 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1750 | Boolean |  | GCP | 1
|  |  | No.5 Outlet Fan | Auto start [GCP] | Digital |  | 1751 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1752 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1753 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1754 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1755 | Boolean |  | GCP | 1
168 | IM14 |  | Overhead crane | Abnormal trip | Digital |  | 1756 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1757 | Boolean |  | GCP | 1
169 | IM15 |  | Air conditioner | Fault | Digital |  | 1758 | Boolean |  | GCP | 1
170 | IM16 |  | Viscosity controller | Fault | Digital |  | 1759 | Boolean |  | GCP | 1
171 | IM29 |  | L.O makeup Pump | Abnormal trip | Digital |  | 1760 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1761 | Boolean |  | GCP | 1
172 | IM19 |  | No.1 Alternator Space heater | Auto start [GCP] | Digital |  | 89 | Boolean |  | GCP#1 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 90 | Boolean |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  | 91 | Boolean |  | GCP#1 | 1
|  |  |  | Running | Digital |  | 92 | Boolean |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  | 93 | Boolean |  | GCP#1 | 1
|  |  | No.2 Alternator Space heater | Auto start [GCP] | Digital |  | 489 | Boolean |  | GCP#2 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 490 | Boolean |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  | 491 | Boolean |  | GCP#2 | 1
|  |  |  | Running | Digital |  | 492 | Boolean |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  | 493 | Boolean |  | GCP#2 | 1
|  |  | No.3 Alternator Space heater | Auto start [GCP] | Digital |  | 889 | Boolean |  | GCP#3 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 890 | Boolean |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  | 891 | Boolean |  | GCP#3 | 1
|  |  |  | Running | Digital |  | 892 | Boolean |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  | 893 | Boolean |  | GCP#3 | 1
|  |  | No.4 Alternator Space heater | Auto start [GCP] | Digital |  | 1289 | Boolean |  | GCP#4 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1290 | Boolean |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  | 1291 | Boolean |  | GCP#4 | 1
|  |  |  | Running | Digital |  | 1292 | Boolean |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  | 1293 | Boolean |  | GCP#4 | 1
173 | IM39 |  | DO unloading pump | Abnormal trip | Digital |  | 1762 | Boolean |  | GCP | 1 |  | LCBD: Start, Stop Push button [manual]
|  |  |  | Running | Digital |  | 1763 | Boolean |  | GCP | 1
174 | IM 22 |  | HO unloading pump | Abnormal trip | Digital |  | 1764 | Boolean |  | GCP | 1 |  | LCBH: Start, Stop Push button [manual]
|  |  |  | Running | Digital |  | 1765 | Boolean |  | GCP | 1
175 | IM18 |  | Inline heater | Auto start [GCP] | Digital |  | 1766 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1767 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1768 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1769 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1770 | Boolean |  | GCP | 1
176 | IM23 |  | HO settling tank heater | Auto start [GCP] | Digital |  | 1771 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1772 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1773 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1774 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1775 | Boolean |  | GCP | 1
177 | IM24 |  | No.1 HO purifier Heater | Fault | Digital |  | 1776 | Boolean |  | GCP | 1
|  |  | No.2 HO purifier Heater | Fault | Digital |  | 1777 | Boolean |  | GCP | 1
178 | IM25 |  | No.1 HO purifier Pump | Abnormal trip | Digital |  | 1778 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1779 | Boolean |  | GCP | 1
|  |  | No.1 HO purifier Pump | Abnormal trip | Digital |  | 1780 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1781 | Boolean |  | GCP | 1
179 | IM27 |  | No.1 HO service tank heater | Auto start [GCP] | Digital |  | 1782 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1783 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1784 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1785 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1786 | Boolean |  | GCP | 1
|  |  | No.2 HO service tank heater | Auto start [GCP] | Digital |  | 1787 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1788 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1789 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1790 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1791 | Boolean |  | GCP | 1
180 | IM17 |  | HO line heater | Fault | Digital |  | 1792 | Boolean |  | GCP | 1
181 | IM28 |  | HO back wash filter | Fault | Digital |  | 1793 | Boolean |  | GCP | 1
182 | I30 |  | No.1 F.O drain tank heater | Auto start [GCP] | Digital |  | 1794 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1795 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1796 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1797 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1798 | Boolean |  | GCP | 1
|  |  | No.2 F.O drain tank heater | Auto start [GCP] | Digital |  | 1799 | Boolean |  | GCP | 1 |  | As per the customer, there's 02 drain pump, maoybe 01 not in use?
|  |  |  | Auto Stop [GCP] | Digital |  | 1800 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1801 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1802 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1803 | Boolean |  | GCP | 1
183 | IM26 |  | No.1 HT Radiator Fan Motor | Auto start [GCP] | Digital |  | 94 | Boolean |  | GCP#1 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 95 | Boolean |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  | 96 | Boolean |  | GCP#1 | 1
|  |  |  | Running | Digital |  | 97 | Boolean |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  | 98 | Boolean |  | GCP#1 | 1
|  |  | No.2 HT Radiator Fan Motor | Auto start [GCP] | Digital |  | 494 | Boolean |  | GCP#2 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 495 | Boolean |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  | 496 | Boolean |  | GCP#2 | 1
|  |  |  | Running | Digital |  | 497 | Boolean |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  | 498 | Boolean |  | GCP#2 | 1
|  |  | No.3 HT Radiator Fan Motor | Auto start [GCP] | Digital |  | 894 | Boolean |  | GCP#3 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 895 | Boolean |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  | 896 | Boolean |  | GCP#3 | 1
|  |  |  | Running | Digital |  | 897 | Boolean |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  | 898 | Boolean |  | GCP#3 | 1
|  |  | No.4 HT Radiator Fan Motor | Auto start [GCP] | Digital |  | 1294 | Boolean |  | GCP#4 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1295 | Boolean |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  | 1296 | Boolean |  | GCP#4 | 1
|  |  |  | Running | Digital |  | 1297 | Boolean |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  | 1298 | Boolean |  | GCP#4 | 1
184 | IM38 |  | No.1 LT Radiator Fan Motor | Auto start [GCP] | Digital |  | 99 | Boolean |  | GCP#1 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 100 | Boolean |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  | 101 | Boolean |  | GCP#1 | 1
|  |  |  | Running | Digital |  | 102 | Boolean |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  | 103 | Boolean |  | GCP#1 | 1
|  |  | No.2 LT Radiator Fan Motor | Auto start [GCP] | Digital |  | 499 | Boolean |  | GCP#2 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 500 | Boolean |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  | 501 | Boolean |  | GCP#2 | 1
|  |  |  | Running | Digital |  | 502 | Boolean |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  | 503 | Boolean |  | GCP#2 | 1
|  |  | No.3 LT Radiator Fan Motor | Auto start [GCP] | Digital |  | 899 | Boolean |  | GCP#3 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 900 | Boolean |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  | 901 | Boolean |  | GCP#3 | 1
|  |  |  | Running | Digital |  | 902 | Boolean |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  | 903 | Boolean |  | GCP#3 | 1
|  |  | No.4 LT Radiator Fan Motor | Auto start [GCP] | Digital |  | 1299 | Boolean |  | GCP#4 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1300 | Boolean |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  | 1301 | Boolean |  | GCP#4 | 1
|  |  |  | Running | Digital |  | 1302 | Boolean |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  | 1303 | Boolean |  | GCP#4 | 1
185 | IM31 |  | Drain discharge pump | Abnormal trip | Digital |  | 1804 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1805 | Boolean |  | GCP | 1
186 | IM32 |  | Make up water pump | Abnormal trip | Digital |  | 1806 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1807 | Boolean |  | GCP | 1
187 | I20 |  | No.1 LO purifier heater | Abnormal trip | Digital |  | 104 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 105 | Boolean |  | GCP | 1
|  |  | No.2 LO purifier heater | Abnormal trip | Digital |  | 504 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 505 | Boolean |  | GCP | 1
|  |  | No.3 LO purifier heater | Abnormal trip | Digital |  | 904 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 905 | Boolean |  | GCP | 1
|  |  | No.4 LO purifier heater | Abnormal trip | Digital |  | 1304 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1305 | Boolean |  | GCP | 1
188 | IM21 |  | No.1 LO purifier pump | Abnormal trip | Digital |  | 106 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 107 | Boolean |  | GCP | 1
|  |  | No.2 LO purifier pump | Abnormal trip | Digital |  | 506 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 507 | Boolean |  | GCP | 1
|  |  | No.3 LO purifier pump | Abnormal trip | Digital |  | 906 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 907 | Boolean |  | GCP | 1
|  |  | No.4 LO purifier pump | Abnormal trip | Digital |  | 1306 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1307 | Boolean |  | GCP | 1
189 | IM34 |  | Sludge transfer pump | Auto start [GCP] | Digital |  | 1824 | Boolean |  | GCP | 1 |  | LCBS: Start, Stop Push button [manual]
|  |  |  | Auto Stop [GCP] | Digital |  | 1825 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1826 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1827 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1828 | Boolean |  | GCP | 1
|  |  | Spare | Auto start [GCP] | Digital |  | 1829 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | 1812 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | 1813 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1832 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | 1833 | Boolean |  | GCP | 1
190 | IM35 |  | No.1 Oily water drain pump | Abnormal trip | Digital |  | 1834 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1835 | Boolean |  | GCP | 1
|  |  | No.2 Oily water drain pump | Abnormal trip | Digital |  | 1836 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1837 | Boolean |  | GCP | 1
191 | IM33 |  | Water supply pump | Abnormal trip | Digital |  | 1838 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | 1839 | Boolean |  | GCP | 1
192 | IM37 |  | Lighting for Engine room | Fault | Digital |  | 1840 | Boolean |  | GCP | 1
193 |  |  | Control Panel | Fault | Digital |  | 1841 | Boolean |  | GCP | 1
194 |  |  | No.1 OMD | Fault | Digital |  | 1842 | Boolean |  | GCP | 1
|  |  | No.2 OMD | Fault | Digital |  | 1843 | Boolean |  | GCP | 1
|  |  | No.3 OMD | Fault | Digital |  | 1844 | Boolean |  | GCP | 1
|  |  | No.4 OMD | Fault | Digital |  | 1845 | Boolean |  | GCP | 1
195 |  |  | Heat trace No.1 | Fault | Digital |  | 1846 | Boolean |  | GCP | 1
|  |  | Heat trace No.2 | Fault | Digital |  | 1847 | Boolean |  | GCP | 1
|  |  | Heat trace No.3 | Fault | Digital |  | 1848 | Boolean |  | GCP | 1
|  |  | Heat trace No.4 | Fault | Digital |  | 1849 | Boolean |  | GCP | 1
|  |  | Heat trace No.5 | Fault | Digital |  | 1850 | Boolean |  | GCP | 1
|  |  | Heat trace No.6 | Fault | Digital |  | 1851 | Boolean |  | GCP | 1
|  |  | Heat trace No.7 | Fault | Digital |  | 1852 | Boolean |  | GCP | 1
|  |  | Heat trace No.8 | Fault | Digital |  | 1853 | Boolean |  | GCP | 1
|  |  | Heat trace No.9 | Fault | Digital |  | 1854 | Boolean |  | GCP | 1
|  |  | Heat trace No.10 | Fault | Digital |  | 1855 | Boolean |  | GCP | 1
|  |  | Heat trace No.11 | Fault | Digital |  | 1856 | Boolean |  | GCP | 1
|  |  | Heat trace No.12 | Fault | Digital |  | 1857 | Boolean |  | GCP | 1
|  |  | Heat trace No.13 | Fault | Digital |  | 1858 | Boolean |  | GCP | 1
|  |  | Heat trace No.14 | Fault | Digital |  | 1859 | Boolean |  | GCP | 1
|  |  | Heat trace No.15 | Fault | Digital |  | 1860 | Boolean |  | GCP | 1
|  |  | Heat trace No.16 | Fault | Digital |  | 1861 | Boolean |  | GCP | 1
|  |  | Heat trace No.17 | Fault | Digital |  | 1862 | Boolean |  | GCP | 1
|  |  | Heat trace No.18 | Fault | Digital |  | 1863 | Boolean |  | GCP | 1
|  |  | Heat trace No.19 | Fault | Digital |  | 1864 | Boolean |  | GCP | 1
|  |  | Heat trace No.20 | Fault | Digital |  | 1865 | Boolean |  | GCP | 1
|  |  | Heat trace No.21 | Fault | Digital |  | 1866 | Boolean |  | GCP | 1
|  |  | Heat trace No.22 | Fault | Digital |  | 1867 | Boolean |  | GCP | 1
|  |  | Heat trace No.23 | Fault | Digital |  | 1868 | Boolean |  | GCP | 1
|  |  | Heat trace No.24 | Fault | Digital |  | 1869 | Boolean |  | GCP | 1
196 |  |  | Drums | Fault | Digital |  |  |  |  | GCP | 1 |  | DRUMS will provide fault dry contacts for DC Supply 1 and DC Supply 2 for its redundant power supply modules and there will be "No GCP connection fault" dry contact as well.
197 | 50,51 | D/G#1 | VCB TRIP(50,51,51N,86,59,27,87G,40,32R,46,81) |  |  |  | 108 | Boolean | 0.5 | GCP#1 | 1
| 50,51 | D/G#2 | VCB TRIP(50,51,51N,86,59,27,87G,40,32R,46,81) |  |  |  | 508 | Boolean | 0.5 | GCP#2 | 1
| 50,51 | D/G#3 | VCB TRIP(50,51,51N,86,59,27,87G,40,32R,46,81) |  |  |  | 908 | Boolean | 0.5 | GCP#3 | 1
| 50,51 | D/G#4 | VCB TRIP(50,51,51N,86,59,27,87G,40,32R,46,81) |  |  |  | 1308 | Boolean | 0.5 | GCP#4 | 1
202 | 59 | D/G#1 | Over Voltage | [5 empty] | 0.5 | GCP#1 | 1
| 59 | D/G#2 | Over Voltage | [5 empty] | 0.5 | GCP#2 | 1
| 59 | D/G#3 | Over Voltage | [5 empty] | 0.5 | GCP#3 | 1
| 59 | D/G#4 | Over Voltage | [5 empty] | 0.5 | GCP#4 | 1
203 | 51N | D/G#1 | Earth Fault | [5 empty] | 0.5 | GCP#1 | 1
| 51N | D/G#2 | Earth Fault | [5 empty] | 0.5 | GCP#2 | 1
| 51N | D/G#3 | Earth Fault | [5 empty] | 0.5 | GCP#3 | 1
| 51N | D/G#4 | Earth Fault | [5 empty] | 0.5 | GCP#4 | 1
204 | 27 | D/G#1 | Under Voltage | [5 empty] | 0.5 | GCP#1 | 1
| 27 | D/G#2 | Under Voltage | [5 empty] | 0.5 | GCP#2 | 1
| 27 | D/G#3 | Under Voltage | [5 empty] | 0.5 | GCP#3 | 1
| 27 | D/G#4 | Under Voltage | [5 empty] | 0.5 | GCP#4 | 1
205 | 87G | D/G#1 | Diff Protection | [5 empty] | 0.5 | GCP#1 | 1
| 87G | D/G#2 | Diff Protection | [5 empty] | 0.5 | GCP#2 | 1
| 87G | D/G#3 | Diff Protection | [5 empty] | 0.5 | GCP#3 | 1
| 87G | D/G#4 | Diff Protection | [5 empty] | 0.5 | GCP#4 | 1
206 | 40 | D/G#1 | Under Excitation | [5 empty] | 0.5 | GCP#1 | 1
| 40 | D/G#2 | Under Excitation | [5 empty] | 0.5 | GCP#2 | 1
| 40 | D/G#3 | Under Excitation | [5 empty] | 0.5 | GCP#3 | 1
| 40 | D/G#4 | Under Excitation | [5 empty] | 0.5 | GCP#4 | 1
207 | 32R | D/G#1 | Reverse Power | [5 empty] | 0.5 | GCP#1 | 1
| 32R | D/G#2 | Reverse Power | [5 empty] | 0.5 | GCP#2 | 1
| 32R | D/G#3 | Reverse Power | [5 empty] | 0.5 | GCP#3 | 1
| 32R | D/G#4 | Reverse Power | [5 empty] | 0.5 | GCP#4 | 1
208 | 81 | D/G#1 | Frequency | [5 empty] | 0.5 | GCP#1 | 1
| 81 | D/G#2 | Frequency | [5 empty] | 0.5 | GCP#2 | 1
| 81 | D/G#3 | Frequency | [5 empty] | 0.5 | GCP#3 | 1
| 81 | D/G#4 | Frequency | [5 empty] | 0.5 | GCP#4 | 1
209 | 46 | D/G#1 | Negative Over Current | [5 empty] | 0.5 | GCP#1 | 1
| 46 | D/G#2 | Negative Over Current | [5 empty] | 0.5 | GCP#2 | 1
| 46 | D/G#3 | Negative Over Current | [5 empty] | 0.5 | GCP#3 | 1
| 46 | D/G#4 | Negative Over Current | [5 empty] | 0.5 | GCP#4 | 1
210 | 86 | D/G#1 | Lockout | [5 empty] | 0.5 | GCP#1 | 1
| 86 | D/G#2 | Lockout | [5 empty] | 0.5 | GCP#2 | 1
| 86 | D/G#3 | Lockout | [5 empty] | 0.5 | GCP#3 | 1
| 86 | D/G#4 | Lockout | [5 empty] | 0.5 | GCP#4 | 1
211 | 50,51 |  | Over Current(LTD,STD,INST) |  |  |  | 1870 | Boolean |  | GCP | 1 |  | Step up feeder
212 | 50,51 |  | Over Current(LTD,STD,INST) |  |  |  | 1871 | Boolean |  | GCP | 1 |  | Step down feeder
213 | 51N |  | Over Current |  |  |  | 1872 | Boolean |  | GCP | 1 |  | NGR
214 | 5E | D/G#1 | Emergency stop local box |  | Digital |  |  |  | 0.5 | Gen Local Box#1 | 1
| 5E | D/G#2 | Emergency stop local box |  | Digital |  |  |  | 0.5 | Gen Local Box#2 | 1
| 5E | D/G#3 | Emergency stop local box |  | Digital |  |  |  | 0.5 | Gen Local Box#3 | 1
| 5E | D/G#4 | Emergency stop local box |  | Digital |  |  |  | 0.5 | Gen Local Box#4 | 1