## Rev05
No. | Device |  | Name | Description | I/O Type | IP address =192.168.100.20 Port = 502 Slave ID = 20 | Modbus Address | Data Type (16 bit Int / Boolean?) | Query Response time (sec) | Location | Qty | Remarks
Terasaki
1 | 12 | D/G#1 | Over Speed | On overspeed [806.4min-1(112%), 828 min-1(115%)] | Digital | IP address =192.168.100.20 Port = 502 Slave ID = 20 | M0 | Boolean | 0.5 | GCP#1 | 1 |  | Engine Trip
| 12 | D/G#2 | Over Speed | On overspeed [806.4min-1(112%), 828 min-1(115%)] | Digital |  | M1000 | Boolean | 0.5 | GCP#2 | 1 |  | Engine Trip
| 12 | D/G#3 | Over Speed | On overspeed [806.4min-1(112%), 828 min-1(115%)] | Digital |  | M2000 | Boolean | 0.5 | GCP#3 | 1 |  | Engine Trip
| 12 | D/G#4 | Over Speed | On overspeed [806.4min-1(112%), 828 min-1(115%)] | Digital |  | M3000 | Boolean | 0.5 | GCP#4 | 1 |  | Engine Trip
2 | 48T | D/G#1 | Engine Start Failure | IN CASE OF (14) KEEPING-OFF AFTER 20 Sec FROM (88V) ACTIVATION | Digital |  | M1 | Boolean | 0.5 | GCP#1 | 1
| 48T | D/G#2 | Engine Start Failure | IN CASE OF (14) KEEPING-OFF AFTER 20 Sec FROM (88V) ACTIVATION | Digital |  | M1001 | Boolean | 0.5 | GCP#2 | 1
| 48T | D/G#3 | Engine Start Failure | IN CASE OF (14) KEEPING-OFF AFTER 20 Sec FROM (88V) ACTIVATION | Digital |  | M2001 | Boolean | 0.5 | GCP#3 | 1
| 48T | D/G#4 | Engine Start Failure | IN CASE OF (14) KEEPING-OFF AFTER 20 Sec FROM (88V) ACTIVATION | Digital |  | M3001 | Boolean | 0.5 | GCP#4 | 1
3 | 26EX2 | D/G#1 | Turbo-charger gas outlet temp switch (2nd) | On over 430°C | Digital |  | M2 | Boolean | 0.5 | GCP#1 | 1 |  | As per "TCTO"(T/C outlet Temp), Engine Trip
| 26EX2 | D/G#2 | Turbo-charger gas outlet temp switch (2nd) | On over 430°C | Digital |  | M1002 | Boolean | 0.5 | GCP#2 | 1 |  | As per "TCTO"(T/C outlet Temp), Engine Trip
| 26EX2 | D/G#3 | Turbo-charger gas outlet temp switch (2nd) | On over 430°C | Digital |  | M2002 | Boolean | 0.5 | GCP#3 | 1 |  | As per "TCTO"(T/C outlet Temp), Engine Trip
| 26EX2 | D/G#4 | Turbo-charger gas outlet temp switch (2nd) | On over 430°C | Digital |  | M3002 | Boolean | 0.5 | GCP#4 | 1 |  | As per "TCTO"(T/C outlet Temp), Engine Trip
4 | MDHH | D/G#1 | Heavy fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "15" | Digital |  | M3 | Boolean | 0.5 | GCP#1 | 1
| MDHH | D/G#2 | Heavy fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "15" | Digital |  | M1003 | Boolean | 0.5 | GCP#2 | 1
| MDHH | D/G#3 | Heavy fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "15" | Digital |  | M2003 | Boolean | 0.5 | GCP#3 | 1
| MDHH | D/G#4 | Heavy fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "15" | Digital |  | M3003 | Boolean | 0.5 | GCP#4 | 1
5 | 63Q2 | D/G#1 | L.O press.switch for engine (2nd) | ON BELOW 0.3MPa | Digital |  | M4 | Boolean | 0.5 | GCP#1 | 1 |  | Engine Trip
| 63Q2 | D/G#2 | L.O press.switch for engine (2nd) | ON BELOW 0.3MPa | Digital |  | M1004 | Boolean | 0.5 | GCP#2 | 1 |  | Engine Trip
| 63Q2 | D/G#3 | L.O press.switch for engine (2nd) | ON BELOW 0.3MPa | Digital |  | M2004 | Boolean | 0.5 | GCP#3 | 1 |  | Engine Trip
| 63Q2 | D/G#4 | L.O press.switch for engine (2nd) | ON BELOW 0.3MPa | Digital |  | M3004 | Boolean | 0.5 | GCP#4 | 1 |  | Engine Trip
6 | 26WJ2 | D/G#1 | Jacket water thermal switch (2nd) | ON OVER 90°C | Digital |  | M5 | Boolean | 0.5 | GCP#1 | 1 |  | Engine Trip
| 26WJ2 | D/G#2 | Jacket water thermal switch (2nd) | ON OVER 90°C | Digital |  | M1005 | Boolean | 0.5 | GCP#2 | 1 |  | Engine Trip
| 26WJ2 | D/G#3 | Jacket water thermal switch (2nd) | ON OVER 90°C | Digital |  | M2005 | Boolean | 0.5 | GCP#3 | 1 |  | Engine Trip
| 26WJ2 | D/G#4 | Jacket water thermal switch (2nd) | ON OVER 90°C | Digital |  | M3005 | Boolean | 0.5 | GCP#4 | 1 |  | Engine Trip
7 | 63QT2 | D/G#1 | L.O press.switch for turbo-charger(2nd) | ON BELOW 0.20MPa | Digital |  | M6 | Boolean | 0.5 | GCP#1 | 1 |  | Engine Trip
| 63QT2 | D/G#2 | L.O press.switch for turbo-charger(2nd) | ON BELOW 0.20MPa | Digital |  | M1006 | Boolean | 0.5 | GCP#2 | 1 |  | Engine Trip
| 63QT2 | D/G#3 | L.O press.switch for turbo-charger(2nd) | ON BELOW 0.20MPa | Digital |  | M2006 | Boolean | 0.5 | GCP#3 | 1 |  | Engine Trip
| 63QT2 | D/G#4 | L.O press.switch for turbo-charger(2nd) | ON BELOW 0.20MPa | Digital |  | M3006 | Boolean | 0.5 | GCP#4 | 1 |  | Engine Trip
8 | 63WJ2 | D/G#1 | Jacket water press.switch (2nd) | ON BELOW 0.1MPa | Digital |  | M7 | Boolean | 0.5 | GCP#1 | 1 |  | Engine Trip
| 63WJ2 | D/G#2 | Jacket water press.switch (2nd) | ON BELOW 0.1MPa | Digital |  | M1007 | Boolean | 0.5 | GCP#2 | 1 |  | Engine Trip
| 63WJ2 | D/G#3 | Jacket water press.switch (2nd) | ON BELOW 0.1MPa | Digital |  | M2007 | Boolean | 0.5 | GCP#3 | 1 |  | Engine Trip
| 63WJ2 | D/G#4 | Jacket water press.switch (2nd) | ON BELOW 0.1MPa | Digital |  | M3007 | Boolean | 0.5 | GCP#4 | 1 |  | Engine Trip
9 |  | D/G#1 | DC control power supply failure |  | Digital |  | M8 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | DC control power supply failure |  | Digital |  | M1008 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | DC control power supply failure |  | Digital |  | M2008 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | DC control power supply failure |  | Digital |  | M3008 | Boolean | 0.5 | GCP#4 | 1
10 |  | D/G#1 | GAC Abnormal |  | Digital |  | M9 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | GAC Abnormal |  | Digital |  | M1009 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | GAC Abnormal |  | Digital |  | M2009 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | GAC Abnormal |  | Digital |  | M3009 | Boolean | 0.5 | GCP#4 | 1
11 | 5E | D/G#1 | Emergency stop |  | Digital |  | M10 | Boolean | 0.5 | GCP#1 | 1 |  | To consider from drums a dry contact to GCP; purpose for the client to activate stop engine/open cb remotely
| 5E | D/G#2 | Emergency stop |  | Digital |  | M1010 | Boolean | 0.5 | GCP#2 | 1 |  | To consider from drums a dry contact to GCP; purpose for the client to activate stop engine/open cb remotely
| 5E | D/G#3 | Emergency stop |  | Digital |  | M2010 | Boolean | 0.5 | GCP#3 | 1 |  | To consider from drums a dry contact to GCP; purpose for the client to activate stop engine/open cb remotely
| 5E | D/G#4 | Emergency stop |  | Digital |  | M3010 | Boolean | 0.5 | GCP#4 | 1 |  | To consider from drums a dry contact to GCP; purpose for the client to activate stop engine/open cb remotely
12 | 69WJ | D/G#1 | Jacket water flow relay | ON BELOW 40m³/h | Digital |  | M11 | Boolean | 0.5 | GCP#1 | 1 |  | Timer 10 Sec
| 69WJ | D/G#2 | Jacket water flow relay | ON BELOW 40m³/h | Digital |  | M1011 | Boolean | 0.5 | GCP#2 | 1 |  | Timer 10 Sec
| 69WJ | D/G#3 | Jacket water flow relay | ON BELOW 40m³/h | Digital |  | M2011 | Boolean | 0.5 | GCP#3 | 1 |  | Timer 10 Sec
| 69WJ | D/G#4 | Jacket water flow relay | ON BELOW 40m³/h | Digital |  | M3011 | Boolean | 0.5 | GCP#4 | 1 |  | Timer 10 Sec
13 |  | D/G#1 | Over voltage |  | Digital |  | M12 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Over voltage |  | Digital |  | M1012 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Over voltage |  | Digital |  | M2012 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Over voltage |  | Digital |  | M3012 | Boolean | 0.5 | GCP#4 | 1
14 |  | D/G#1 | Under voltage |  | Digital |  | M13 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Under voltage |  | Digital |  | M1013 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Under voltage |  | Digital |  | M2013 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Under voltage |  | Digital |  | M3013 | Boolean | 0.5 | GCP#4 | 1
15 |  | D/G#1 | Gen differential |  | Digital |  | M14 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Gen differential |  | Digital |  | M1014 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Gen differential |  | Digital |  | M2014 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Gen differential |  | Digital |  | M3014 | Boolean | 0.5 | GCP#4 | 1
16 |  | D/G#1 | Reverse power |  | Digital |  | M15 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Reverse power |  | Digital |  | M1015 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Reverse power |  | Digital |  | M2015 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Reverse power |  | Digital |  | M3015 | Boolean | 0.5 | GCP#4 | 1
17 |  | D/G#1 | Field failure |  | Digital |  | M16 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Field failure |  | Digital |  | M1016 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Field failure |  | Digital |  | M2016 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Field failure |  | Digital |  | M3016 | Boolean | 0.5 | GCP#4 | 1
18 | MDH | D/G#1 | Light fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "10" | Digital |  | M17 | Boolean | 0.5 | GCP#1 | 1
| MDH | D/G#2 | Light fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "10" | Digital |  | M1017 | Boolean | 0.5 | GCP#2 | 1
| MDH | D/G#3 | Light fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "10" | Digital |  | M2017 | Boolean | 0.5 | GCP#3 | 1
| MDH | D/G#4 | Light fault of oil mist detector | ON WHEN OIL MIST LEVEL RED: "10" | Digital |  | M3017 | Boolean | 0.5 | GCP#4 | 1
19 | MDSY | D/G#1 | Light fault of oil mist detector system failure | ON WHEN SYSTEM FAILURE OCCURS | Digital |  | M18 | Boolean | 0.5 | GCP#1 | 1
| MDSY | D/G#2 | Light fault of oil mist detector system failure | ON WHEN SYSTEM FAILURE OCCURS | Digital |  | M1018 | Boolean | 0.5 | GCP#2 | 1
| MDSY | D/G#3 | Light fault of oil mist detector system failure | ON WHEN SYSTEM FAILURE OCCURS | Digital |  | M2018 | Boolean | 0.5 | GCP#3 | 1
| MDSY | D/G#4 | Light fault of oil mist detector system failure | ON WHEN SYSTEM FAILURE OCCURS | Digital |  | M3018 | Boolean | 0.5 | GCP#4 | 1
20 | 63Q1 | D/G#1 | LO press.switch for engine(1st) | ON BELOW 0.35MPa | Digital |  | M19 | Boolean | 0.5 | GCP#1 | 1 |  | As per "PTLO"
| 63Q1 | D/G#2 | LO press.switch for engine(1st) | ON BELOW 0.35MPa | Digital |  | M1019 | Boolean | 0.5 | GCP#2 | 1 |  | As per "PTLO"
| 63Q1 | D/G#3 | LO press.switch for engine(1st) | ON BELOW 0.35MPa | Digital |  | M2019 | Boolean | 0.5 | GCP#3 | 1 |  | As per "PTLO"
| 63Q1 | D/G#4 | LO press.switch for engine(1st) | ON BELOW 0.35MPa | Digital |  | M3019 | Boolean | 0.5 | GCP#4 | 1 |  | As per "PTLO"
21 | 63QP | D/G#1 | LO press.switch for priming | ON OVER 0.03MPa | Digital |  | M20 | Boolean | 0.5 | GCP#1 | 1 |  | NO PRESS. AFTER 60-90sec. FROM PUMP START
| 63QP | D/G#2 | LO press.switch for priming | ON OVER 0.03MPa | Digital |  | M1020 | Boolean | 0.5 | GCP#2 | 1 |  | NO PRESS. AFTER 60-90sec. FROM PUMP START
| 63QP | D/G#3 | LO press.switch for priming | ON OVER 0.03MPa | Digital |  | M2020 | Boolean | 0.5 | GCP#3 | 1 |  | NO PRESS. AFTER 60-90sec. FROM PUMP START
| 63QP | D/G#4 | LO press.switch for priming | ON OVER 0.03MPa | Digital |  | M3020 | Boolean | 0.5 | GCP#4 | 1 |  | NO PRESS. AFTER 60-90sec. FROM PUMP START
22 | 63WC | D/G#1 | Cooler water press switch | ON BELOW 0.1MPa | Digital |  | M21 | Boolean | 0.5 | GCP#1 | 1 |  | As per "PTCW"
| 63WC | D/G#2 | Cooler water press switch | ON BELOW 0.1MPa | Digital |  | M1021 | Boolean | 0.5 | GCP#2 | 1 |  | As per "PTCW"
| 63WC | D/G#3 | Cooler water press switch | ON BELOW 0.1MPa | Digital |  | M2021 | Boolean | 0.5 | GCP#3 | 1 |  | As per "PTCW"
| 63WC | D/G#4 | Cooler water press switch | ON BELOW 0.1MPa | Digital |  | M3021 | Boolean | 0.5 | GCP#4 | 1 |  | As per "PTCW"
23 | 63QT1 | D/G#1 | L.O. press switch for turbo-charger (1st) | ON BELOW 0.25MPa | Digital |  | M22 | Boolean | 0.5 | GCP#1 | 1 |  | As per "PTTLO"
| 63QT1 | D/G#2 | L.O. press switch for turbo-charger (1st) | ON BELOW 0.25MPa | Digital |  | M1022 | Boolean | 0.5 | GCP#2 | 1 |  | As per "PTTLO"
| 63QT1 | D/G#3 | L.O. press switch for turbo-charger (1st) | ON BELOW 0.25MPa | Digital |  | M2022 | Boolean | 0.5 | GCP#3 | 1 |  | As per "PTTLO"
| 63QT1 | D/G#4 | L.O. press switch for turbo-charger (1st) | ON BELOW 0.25MPa | Digital |  | M3022 | Boolean | 0.5 | GCP#4 | 1 |  | As per "PTTLO"
24 | 26WJ1 | D/G#1 | Jacket water thermal switch (1st) | ON OVER 85°C | Digital |  | M23 | Boolean | 0.5 | GCP#1 | 1 |  | As per "TRJWO"
| 26WJ1 | D/G#2 | Jacket water thermal switch (1st) | ON OVER 85°C | Digital |  | M1023 | Boolean | 0.5 | GCP#2 | 1 |  | As per "TRJWO"
| 26WJ1 | D/G#3 | Jacket water thermal switch (1st) | ON OVER 85°C | Digital |  | M2023 | Boolean | 0.5 | GCP#3 | 1 |  | As per "TRJWO"
| 26WJ1 | D/G#4 | Jacket water thermal switch (1st) | ON OVER 85°C | Digital |  | M3023 | Boolean | 0.5 | GCP#4 | 1 |  | As per "TRJWO"
25 | 26WC | D/G#1 | Cooler water thermal switch | ON OVER 50°C | Digital |  | M24 | Boolean | 0.5 | GCP#1 | 1
| 26WC | D/G#2 | Cooler water thermal switch | ON OVER 50°C | Digital |  | M1024 | Boolean | 0.5 | GCP#2 | 1
| 26WC | D/G#3 | Cooler water thermal switch | ON OVER 50°C | Digital |  | M2024 | Boolean | 0.5 | GCP#3 | 1
| 26WC | D/G#4 | Cooler water thermal switch | ON OVER 50°C | Digital |  | M3024 | Boolean | 0.5 | GCP#4 | 1
26 | 26Q | D/G#1 | L.O. thermal switch | ON OVER 65°C | Digital |  | M25 | Boolean | 0.5 | GCP#1 | 1
| 26Q | D/G#2 | L.O. thermal switch | ON OVER 65°C | Digital |  | M1025 | Boolean | 0.5 | GCP#2 | 1
| 26Q | D/G#3 | L.O. thermal switch | ON OVER 65°C | Digital |  | M2025 | Boolean | 0.5 | GCP#3 | 1
| 26Q | D/G#4 | L.O. thermal switch | ON OVER 65°C | Digital |  | M3025 | Boolean | 0.5 | GCP#4 | 1
27 | 33QSL | D/G#1 | L.O. sump tank level switch | ON BELOW LOWER LIMIT | Digital |  | M26 | Boolean | 0.5 | GCP#1 | 1 |  | Timer 5 sec
| 33QSL | D/G#2 | L.O. sump tank level switch | ON BELOW LOWER LIMIT | Digital |  | M1026 | Boolean | 0.5 | GCP#2 | 1 |  | Timer 5 sec
| 33QSL | D/G#3 | L.O. sump tank level switch | ON BELOW LOWER LIMIT | Digital |  | M2026 | Boolean | 0.5 | GCP#3 | 1 |  | Timer 5 sec
| 33QSL | D/G#4 | L.O. sump tank level switch | ON BELOW LOWER LIMIT | Digital |  | M3026 | Boolean | 0.5 | GCP#4 | 1 |  | Timer 5 sec
28 | 63WJ1 | D/G#1 | Jacket water press switch (1st) | ON BELOW 0.15MPa | Digital |  | M27 | Boolean | 0.5 | GCP#1 | 1 |  | As per "PTJW"
| 63WJ1 | D/G#2 | Jacket water press switch (1st) | ON BELOW 0.15MPa | Digital |  | M1027 | Boolean | 0.5 | GCP#2 | 1 |  | As per "PTJW"
| 63WJ1 | D/G#3 | Jacket water press switch (1st) | ON BELOW 0.15MPa | Digital |  | M2027 | Boolean | 0.5 | GCP#3 | 1 |  | As per "PTJW"
| 63WJ1 | D/G#4 | Jacket water press switch (1st) | ON BELOW 0.15MPa | Digital |  | M3027 | Boolean | 0.5 | GCP#4 | 1 |  | As per "PTJW"
29 | 63QD | D/G#1 | L.O. filter differential press switch | ON OVER 0.09MPa | Digital |  | M28 | Boolean | 0.5 | GCP#1 | 1
| 63QD | D/G#2 | L.O. filter differential press switch | ON OVER 0.09MPa | Digital |  | M1028 | Boolean | 0.5 | GCP#2 | 1
| 63QD | D/G#3 | L.O. filter differential press switch | ON OVER 0.09MPa | Digital |  | M2028 | Boolean | 0.5 | GCP#3 | 1
| 63QD | D/G#4 | L.O. filter differential press switch | ON OVER 0.09MPa | Digital |  | M3028 | Boolean | 0.5 | GCP#4 | 1
30 | 63QTD | D/G#1 | T/C L.O filter differential press switch | ON OVER 0.06MPa | Digital |  | M29 | Boolean | 0.5 | GCP#1 | 1
| 63QTD | D/G#2 | T/C L.O filter differential press switch | ON OVER 0.06MPa | Digital |  | M1029 | Boolean | 0.5 | GCP#2 | 1
| 63QTD | D/G#3 | T/C L.O filter differential press switch | ON OVER 0.06MPa | Digital |  | M2029 | Boolean | 0.5 | GCP#3 | 1
| 63QTD | D/G#4 | T/C L.O filter differential press switch | ON OVER 0.06MPa | Digital |  | M3029 | Boolean | 0.5 | GCP#4 | 1
31 | 33HF | D/G#1 | F.O leak tank level switch | ON OVER UPPER LIMIT | Digital |  | M30 | Boolean | 0.5 | GCP#1 | 1 |  | Timer 5 sec
| 33HF | D/G#2 | F.O leak tank level switch | ON OVER UPPER LIMIT | Digital |  | M1030 | Boolean | 0.5 | GCP#2 | 1 |  | Timer 5 sec
| 33HF | D/G#3 | F.O leak tank level switch | ON OVER UPPER LIMIT | Digital |  | M2030 | Boolean | 0.5 | GCP#3 | 1 |  | Timer 5 sec
| 33HF | D/G#4 | F.O leak tank level switch | ON OVER UPPER LIMIT | Digital |  | M3030 | Boolean | 0.5 | GCP#4 | 1 |  | Timer 5 sec
32 | TCTO | D/G#1 | EXH. GAS T/C OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3000 | 16 bit Int | 0.5 | GCP#1 | 1 |  | As per "TCTO"
| TCTO | D/G#2 | EXH. GAS T/C OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3100 | 16 bit Int | 0.5 | GCP#2 | 1 |  | As per "TCTO"
| TCTO | D/G#3 | EXH. GAS T/C OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3200 | 16 bit Int | 0.5 | GCP#3 | 1 |  | As per "TCTO"
| TCTO | D/G#4 | EXH. GAS T/C OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3300 | 16 bit Int | 0.5 | GCP#4 | 1 |  | As per "TCTO"
33 | 69WC | D/G#1 | Cooler water flow relay | ON BELOW 40m³/h | Digital |  | M31 | Boolean | 0.5 | GCP#1 | 1 |  | Timer 10 sec
| 69WC | D/G#2 | Cooler water flow relay | ON BELOW 40m³/h | Digital |  | M1031 | Boolean | 0.5 | GCP#2 | 1 |  | Timer 10 sec
| 69WC | D/G#3 | Cooler water flow relay | ON BELOW 40m³/h | Digital |  | M2031 | Boolean | 0.5 | GCP#3 | 1 |  | Timer 10 sec
| 69WC | D/G#4 | Cooler water flow relay | ON BELOW 40m³/h | Digital |  | M3031 | Boolean | 0.5 | GCP#4 | 1 |  | Timer 10 sec
34 | 63AC |  | Air receiver press switch for engine | On: Below 2.16MPa, Off: 2.94MPa | Digital |  | M4000 | Boolean | 0.5 | GCP | 1
| 63AC |  | Air receiver press switch for engine | On: Below 2.16MPa, Off: 2.94MPa | Digital |  | M4001 | Boolean | 0.5 | GCP | 1
| 63AC |  | Air receiver press switch for engine | On: Below 2.16MPa, Off: 2.94MPa | Digital |  | M4002 | Boolean | 0.5 | GCP | 1
35 | 63AL |  | Air receiver press switch for engine | On: Below 1.77MPa | Digital |  | M4003 | Boolean | 0.5 | GCP | 1
| 63AL |  | Air receiver press switch for engine | On: Below 1.77MPa | Digital |  | M4004 | Boolean | 0.5 | GCP | 1
| 63AL |  | Air receiver press switch for engine | On: Below 1.77MPa | Digital |  | M4005 | Boolean | 0.5 | GCP | 1
36 | 33WCH | D/G#1 | Level switch for C.W. expansion tank | On: above ___L, | Digital |  | M32 | Boolean | 0.5 | GCP#1 | 1
| 33WCH | D/G#2 | Level switch for C.W. expansion tank | On: above ___L, | Digital |  | M1032 | Boolean | 0.5 | GCP#2 | 1
| 33WCH | D/G#3 | Level switch for C.W. expansion tank | On: above ___L, | Digital |  | M2032 | Boolean | 0.5 | GCP#3 | 1
| 33WCH | D/G#4 | Level switch for C.W. expansion tank | On: above ___L, | Digital |  | M3032 | Boolean | 0.5 | GCP#4 | 1
37 | 33WCL | D/G#1 | Level switch for C.W. expansion tank | On: below ___L, | Digital |  | M33 | Boolean | 0.5 | GCP#1 | 1
| 33WCL | D/G#2 | Level switch for C.W. expansion tank | On: below ___L, | Digital |  | M1033 | Boolean | 0.5 | GCP#2 | 1
| 33WCL | D/G#3 | Level switch for C.W. expansion tank | On: below ___L, | Digital |  | M2033 | Boolean | 0.5 | GCP#3 | 1
| 33WCL | D/G#4 | Level switch for C.W. expansion tank | On: below ___L, | Digital |  | M3033 | Boolean | 0.5 | GCP#4 | 1
38 | 33WJH | D/G#1 | Level switch for J.W. expansion tank | On: above ___L, | Digital |  | M34 | Boolean | 0.5 | GCP#1 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJH | D/G#2 | Level switch for J.W. expansion tank | On: above ___L, | Digital |  | M1034 | Boolean | 0.5 | GCP#2 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJH | D/G#3 | Level switch for J.W. expansion tank | On: above ___L, | Digital |  | M2034 | Boolean | 0.5 | GCP#3 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJH | D/G#4 | Level switch for J.W. expansion tank | On: above ___L, | Digital |  | M3034 | Boolean | 0.5 | GCP#4 | 1 |  | Sensor by Ormin, timer 5 sec
39 | 33WJL | D/G#1 | Level switch for J.W. expansion tank | On: below ___L, | Digital |  | M35 | Boolean | 0.5 | GCP#1 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJL | D/G#2 | Level switch for J.W. expansion tank | On: below ___L, | Digital |  | M1035 | Boolean | 0.5 | GCP#2 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJL | D/G#3 | Level switch for J.W. expansion tank | On: below ___L, | Digital |  | M2035 | Boolean | 0.5 | GCP#3 | 1 |  | Sensor by Ormin, timer 5 sec
| 33WJL | D/G#4 | Level switch for J.W. expansion tank | On: below ___L, | Digital |  | M3035 | Boolean | 0.5 | GCP#4 | 1 |  | Sensor by Ormin, timer 5 sec
40 | 33FDH | D/G#1 | Level switch for DO service tank level high | On: above ___L, | Digital |  | M36 | Boolean | 0.5 | GCP#1 | 1 |  | timer 5 sec
| 33FDH | D/G#2 | Level switch for DO service tank level high | On: above ___L, | Digital |  | M1036 | Boolean | 0.5 | GCP#2 | 1 |  | timer 5 sec
| 33FDH | D/G#3 | Level switch for DO service tank level high | On: above ___L, | Digital |  | M2036 | Boolean | 0.5 | GCP#3 | 1 |  | timer 5 sec
| 33FDH | D/G#4 | Level switch for DO service tank level high | On: above ___L, | Digital |  | M3036 | Boolean | 0.5 | GCP#4 | 1 |  | timer 5 sec
41 | 33FDL | D/G#1 | Level switch for DO service tank level low | On: below ___L, | Digital |  | M37 | Boolean | 0.5 | GCP#1 | 1 |  | timer 5 sec
| 33FDL | D/G#2 | Level switch for DO service tank level low | On: below ___L, | Digital |  | M1037 | Boolean | 0.5 | GCP#2 | 1 |  | timer 5 sec
| 33FDL | D/G#3 | Level switch for DO service tank level low | On: below ___L, | Digital |  | M2037 | Boolean | 0.5 | GCP#3 | 1 |  | timer 5 sec
| 33FDL | D/G#4 | Level switch for DO service tank level low | On: below ___L, | Digital |  | M3037 | Boolean | 0.5 | GCP#4 | 1 |  | timer 5 sec
42 | 33FDC | D/G | Level switch for DO service tank level control | On: below ___L, Off: above ____L | Digital |  | M4006 | Boolean | 0.5 | GCP | 1 |  | timer 5 sec
43 | 33SETH | D/G | Level switch for HO settling tank level high | On: above ___L, | Digital |  | M4007 | Boolean | 0.5 | GCP | 1 |  | timer 5 sec
44 | 33SETL | D/G | Level switch for HO settling tank level low | On: below ___L, | Digital |  | M4008 | Boolean | 0.5 | GCP | 1 |  | timer 5 sec
45 | 33SETC | D/G | Level switch for HO settling tank level control | On: below ___L, Off: above ____L | Digital |  | M4009 | Boolean | 0.5 | GCP | 1 |  | timer 5 sec
46 | 33SEL | D/G | Level switch for HO service tank level low | On: below ___L, | Digital |  | M4010 | Boolean | 0.5 | GCP | 1 |  | timer 5 sec
47 | 63F | D/G#1 | F.O press.switch | ON BELOW 0.15MPa | Digital |  | M38 | Boolean | 0.5 | GCP#1 | 1 |  | As per "PTFO"
| 63F | D/G#2 | F.O press.switch | ON BELOW 0.15MPa | Digital |  | M1038 | Boolean | 0.5 | GCP#2 | 1 |  | As per "PTFO"
| 63F | D/G#3 | F.O press.switch | ON BELOW 0.15MPa | Digital |  | M2038 | Boolean | 0.5 | GCP#3 | 1 |  | As per "PTFO"
| 63F | D/G#4 | F.O press.switch | ON BELOW 0.15MPa | Digital |  | M3038 | Boolean | 0.5 | GCP#4 | 1 |  | As per "PTFO"
48 | 33FDRC | D/G | Level switch for F.O drain tank level control | On: below ___L, Off: above ____L | Digital |  | M4011 | Boolean | 0.5 | GCP | 1
49 | 33FDRH | D/G | Level switch for F.O drain tank | On: above ___L, | Digital |  | M4012 | Boolean | 0.5 | GCP | 1
50 | 63FB | D/G | Press switch for auto back wash filter | ON OVER 0.06MPa | Digital |  | M4013 | Boolean | 0.5 | D/G | 1
51 |  | D/G#1 | Display failure |  | Digital |  | M39 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Display failure |  | Digital |  | M1039 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Display failure |  | Digital |  | M2039 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Display failure |  | Digital |  | M3039 | Boolean | 0.5 | GCP#4 | 1
52 |  | D/G#1 | DC100V source abnormal |  | Digital |  | M40 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | DC100V source abnormal |  | Digital |  | M1040 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | DC100V source abnormal |  | Digital |  | M2040 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | DC100V source abnormal |  | Digital |  | M3040 | Boolean | 0.5 | GCP#4 | 1
53 |  | D/G#1 | DC24V source abnormal |  | Digital |  | M41 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | DC24V source abnormal |  | Digital |  | M1041 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | DC24V source abnormal |  | Digital |  | M2041 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | DC24V source abnormal |  | Digital |  | M3041 | Boolean | 0.5 | GCP#4 | 1
54 |  | D/G#1 | Auto synchro failure |  | Digital |  | M42 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Auto synchro failure |  | Digital |  | M1042 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Auto synchro failure |  | Digital |  | M2042 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Auto synchro failure |  | Digital |  | M3042 | Boolean | 0.5 | GCP#4 | 1
55 |  | D/G#1 | CB non-close |  | Digital |  | M43 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | CB non-close |  | Digital |  | M1043 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | CB non-close |  | Digital |  | M2043 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | CB non-close |  | Digital |  | M3043 | Boolean | 0.5 | GCP#4 | 1
56 | 63AS |  | Control air press.switch | ON BELOW 0.60MPa | Digital |  | M4014 | Boolean | 0.5 | GCP | 1 |  | Timer 10 sec
| 63AS |  | Control air press.switch | ON BELOW 0.60MPa | Digital |  | M4015 | Boolean | 0.5 | GCP | 1 |  | Timer 10 sec
| 63AS |  | Control air press.switch | ON BELOW 0.60MPa | Digital |  | M4016 | Boolean | 0.5 | GCP | 1 |  | Timer 10 sec
| 63AS |  | Control air press.switch | ON BELOW 0.60MPa | Digital |  | M4017 | Boolean | 0.5 | GCP | 1 |  | Timer 10 sec
60 | 12M | D/G#1 | Over Speed (mechanical side) | ON OVER 113% (+0%, -3%) [813.6min-1(113%)] | Digital |  | M44 | Boolean | 0.5 | D/G#1 | 1
| 12M | D/G#2 | Over Speed (mechanical side) | ON OVER 113% (+0%, -3%) [813.6min-1(113%)] | Digital |  | M1044 | Boolean | 0.5 | D/G#2 | 1
| 12M | D/G#3 | Over Speed (mechanical side) | ON OVER 113% (+0%, -3%) [813.6min-1(113%)] | Digital |  | M2044 | Boolean | 0.5 | D/G#3 | 1
| 12M | D/G#4 | Over Speed (mechanical side) | ON OVER 113% (+0%, -3%) [813.6min-1(113%)] | Digital |  | M3044 | Boolean | 0.5 | D/G#4 | 1
61 | 26G1 | D/G#1 | Thermal switch for alternator beaing(Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | M45 | Boolean | 0.5 | GCP#1 | 1
| 26G1 | D/G#2 | Thermal switch for alternator beaing(Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | M1045 | Boolean | 0.5 | GCP#2 | 1
| 26G1 | D/G#3 | Thermal switch for alternator beaing(Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | M2045 | Boolean | 0.5 | GCP#3 | 1
| 26G1 | D/G#4 | Thermal switch for alternator beaing(Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | M3045 | Boolean | 0.5 | GCP#4 | 1
62 | 26G2 | D/G#1 | Thermal switch for alternator beaing (Anti-Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | M46 | Boolean | 0.5 | GCP#1 | 1
| 26G2 | D/G#2 | Thermal switch for alternator beaing (Anti-Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | M1046 | Boolean | 0.5 | GCP#2 | 1
| 26G2 | D/G#3 | Thermal switch for alternator beaing (Anti-Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | M2046 | Boolean | 0.5 | GCP#3 | 1
| 26G2 | D/G#4 | Thermal switch for alternator beaing (Anti-Fly-wheel side) | ON OVER THE UPPER LIMIT | Digital |  | M3046 | Boolean | 0.5 | GCP#4 | 1
65 | 13 | D/G#1 | RATED SPEED | ON OVER 90% [648min-1(90%)] | Digital |  | M47 | Boolean | 0.5 | GCP#1 | 1
| 13 | D/G#2 | RATED SPEED | ON OVER 90% [648min-1(90%)] | Digital |  | M1047 | Boolean | 0.5 | GCP#2 | 1
| 13 | D/G#3 | RATED SPEED | ON OVER 90% [648min-1(90%)] | Digital |  | M2047 | Boolean | 0.5 | GCP#3 | 1
| 13 | D/G#4 | RATED SPEED | ON OVER 90% [648min-1(90%)] | Digital |  | M3047 | Boolean | 0.5 | GCP#4 | 1
66 | 14 | D/G#1 | LOW SPEED | ON OVER 300min-1[300min-1(41.67%)] | Digital |  | M48 | Boolean | 0.5 | GCP#1 | 1
| 14 | D/G#2 | LOW SPEED | ON OVER 300min-1[300min-1(41.67%)] | Digital |  | M1048 | Boolean | 0.5 | GCP#2 | 1
| 14 | D/G#3 | LOW SPEED | ON OVER 300min-1[300min-1(41.67%)] | Digital |  | M2048 | Boolean | 0.5 | GCP#3 | 1
| 14 | D/G#4 | LOW SPEED | ON OVER 300min-1[300min-1(41.67%)] | Digital |  | M3048 | Boolean | 0.5 | GCP#4 | 1
67 | 88V | D/G#1 | STARTING SOLENOID VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | M49 | Boolean | 0.5 | GCP#1 | 1
| 88V | D/G#2 | STARTING SOLENOID VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | M1049 | Boolean | 0.5 | GCP#2 | 1
| 88V | D/G#3 | STARTING SOLENOID VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | M2049 | Boolean | 0.5 | GCP#3 | 1
| 88V | D/G#4 | STARTING SOLENOID VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | M3049 | Boolean | 0.5 | GCP#4 | 1
68 | 5V | D/G#1 | FUEL SHUT DOWN DEVICE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | M50 | Boolean | 0.5 | GCP#1 | 1
| 5V | D/G#2 | FUEL SHUT DOWN DEVICE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | M1050 | Boolean | 0.5 | GCP#2 | 1
| 5V | D/G#3 | FUEL SHUT DOWN DEVICE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | M2050 | Boolean | 0.5 | GCP#3 | 1
| 5V | D/G#4 | FUEL SHUT DOWN DEVICE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | M3050 | Boolean | 0.5 | GCP#4 | 1
69 | 88L | D/G#1 | FUEL CONTROL PISTON MAGNETIC VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | M51 | Boolean | 0.5 | GCP#1 | 1
| 88L | D/G#2 | FUEL CONTROL PISTON MAGNETIC VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | M1051 | Boolean | 0.5 | GCP#2 | 1
| 88L | D/G#3 | FUEL CONTROL PISTON MAGNETIC VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | M2051 | Boolean | 0.5 | GCP#3 | 1
| 88L | D/G#4 | FUEL CONTROL PISTON MAGNETIC VALVE | WHEN START ENGINE, VALVE OPEN BY EXCITING DC24V, 15W | Digital |  | M3051 | Boolean | 0.5 | GCP#4 | 1
70 | 5S | D/G#1 | FUEL OIL CUT PISTON MAGNETIC VALVE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | M52 | Boolean | 0.5 | GCP#1 | 1
| 5S | D/G#2 | FUEL OIL CUT PISTON MAGNETIC VALVE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | M1052 | Boolean | 0.5 | GCP#2 | 1
| 5S | D/G#3 | FUEL OIL CUT PISTON MAGNETIC VALVE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | M2052 | Boolean | 0.5 | GCP#3 | 1
| 5S | D/G#4 | FUEL OIL CUT PISTON MAGNETIC VALVE | WHEN STOP ENGINE, VALVE SHUT BY EXCITING DC24V, 15W | Digital |  | M3052 | Boolean | 0.5 | GCP#4 | 1
71 | MDMO | D/G#1 | MONITORING OF OIL MIST LEVEL | 0-2.0mg/L_4-20mA | Analog |  | D3001 | 16 bit Int | 0.5 | GCP#1 | 1
| MDMO | D/G#2 | MONITORING OF OIL MIST LEVEL | 0-2.0mg/L_4-20mA | Analog |  | D3101 | 16 bit Int | 0.5 | GCP#2 | 1
| MDMO | D/G#3 | MONITORING OF OIL MIST LEVEL | 0-2.0mg/L_4-20mA | Analog |  | D3201 | 16 bit Int | 0.5 | GCP#3 | 1
| MDMO | D/G#4 | MONITORING OF OIL MIST LEVEL | 0-2.0mg/L_4-20mA | Analog |  | D3301 | 16 bit Int | 0.5 | GCP#4 | 1
72 | HS | D/G#1 | GOVERNOR HANDLE SWITCH | ON: ENGINE START CONDITION | Digital |  | M53 | Boolean | 0.5 | GCP#1 | 1
| HS | D/G#2 | GOVERNOR HANDLE SWITCH | ON: ENGINE START CONDITION | Digital |  | M1053 | Boolean | 0.5 | GCP#2 | 1
| HS | D/G#3 | GOVERNOR HANDLE SWITCH | ON: ENGINE START CONDITION | Digital |  | M2053 | Boolean | 0.5 | GCP#3 | 1
| HS | D/G#4 | GOVERNOR HANDLE SWITCH | ON: ENGINE START CONDITION | Digital |  | M3053 | Boolean | 0.5 | GCP#4 | 1
73 | 33T | D/G#1 | TURNING HANDLE POSITION SWITCH(ON AT TURNING DEVICE OUT) | ON: ENGINE START CONDITION | Digital |  | M54 | Boolean | 0.5 | GCP#1 | 1
| 33T | D/G#2 | TURNING HANDLE POSITION SWITCH(ON AT TURNING DEVICE OUT) | ON: ENGINE START CONDITION | Digital |  | M1054 | Boolean | 0.5 | GCP#2 | 1
| 33T | D/G#3 | TURNING HANDLE POSITION SWITCH(ON AT TURNING DEVICE OUT) | ON: ENGINE START CONDITION | Digital |  | M2054 | Boolean | 0.5 | GCP#3 | 1
| 33T | D/G#4 | TURNING HANDLE POSITION SWITCH(ON AT TURNING DEVICE OUT) | ON: ENGINE START CONDITION | Digital |  | M3054 | Boolean | 0.5 | GCP#4 | 1
74 | 1B(U) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | D3002 | 16 bit Int | 0.5 | GCP#1 | 1
| 1B(U) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | D3102 | 16 bit Int | 0.5 | GCP#2 | 1
| 1B(U) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | D3202 | 16 bit Int | 0.5 | GCP#3 | 1
| 1B(U) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | D3302 | 16 bit Int | 0.5 | GCP#4 | 1
75 | 2B(V) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | D3003 | 16 bit Int | 0.5 | GCP#1 | 1
| 2B(V) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | D3103 | 16 bit Int | 0.5 | GCP#2 | 1
| 2B(V) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | D3203 | 16 bit Int | 0.5 | GCP#3 | 1
| 2B(V) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | D3303 | 16 bit Int | 0.5 | GCP#4 | 1
76 | 3B(W) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | D3004 | 16 bit Int | 0.5 | GCP#1 | 1
| 3B(W) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | D3104 | 16 bit Int | 0.5 | GCP#2 | 1
| 3B(W) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | D3204 | 16 bit Int | 0.5 | GCP#3 | 1
| 3B(W) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (WORK) | Analog |  | D3304 | 16 bit Int | 0.5 | GCP#4 | 1
77 | 4B(U) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#1 | 1
| 4B(U) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#2 | 1
| 4B(U) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#3 | 1
| 4B(U) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#4 | 1
78 | 5B(V) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#1 | 1
| 5B(V) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#2 | 1
| 5B(V) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#3 | 1
| 5B(V) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#4 | 1
79 | 6B(W) | D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#1 | 1
| 6B(W) | D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#2 | 1
| 6B(W) | D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#3 | 1
| 6B(W) | D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | PT 100Ω @ 0°C (SPARE) | Analog |  |  |  | 0.5 | GCP#4 | 1
80 | 38G1 | D/G#1 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | D3005 | 16 bit Int | 0.5 | GCP#1 | 1
| 38G1 | D/G#2 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | D3105 | 16 bit Int | 0.5 | GCP#2 | 1
| 38G1 | D/G#3 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | D3205 | 16 bit Int | 0.5 | GCP#3 | 1
| 38G1 | D/G#4 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | D3305 | 16 bit Int | 0.5 | GCP#4 | 1
81 | 38G2 | D/G#1 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | D3006 | 16 bit Int | 0.5 | GCP#1 | 1
| 38G2 | D/G#2 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | D3106 | 16 bit Int | 0.5 | GCP#2 | 1
| 38G2 | D/G#3 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | D3206 | 16 bit Int | 0.5 | GCP#3 | 1
| 38G2 | D/G#4 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | PT 100Ω @ 0°C | Analog |  | D3306 | 16 bit Int | 0.5 | GCP#4 | 1
82 | TC1 | D/G#1 | EXH. GAS No. 1 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3007 | 16 bit Int | 0.5 | GCP#1 | 1
| TC1 | D/G#2 | EXH. GAS No. 1 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3107 | 16 bit Int | 0.5 | GCP#2 | 1
| TC1 | D/G#3 | EXH. GAS No. 1 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3207 | 16 bit Int | 0.5 | GCP#3 | 1
| TC1 | D/G#4 | EXH. GAS No. 1 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3307 | 16 bit Int | 0.5 | GCP#4 | 1
83 | TC2 | D/G#1 | EXH. GAS No. 2 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3008 | 16 bit Int | 0.5 | GCP#1 | 1
| TC2 | D/G#2 | EXH. GAS No. 2 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3108 | 16 bit Int | 0.5 | GCP#2 | 1
| TC2 | D/G#3 | EXH. GAS No. 2 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3208 | 16 bit Int | 0.5 | GCP#3 | 1
| TC2 | D/G#4 | EXH. GAS No. 2 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3308 | 16 bit Int | 0.5 | GCP#4 | 1
84 | TC3 | D/G#1 | EXH. GAS No. 3 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3009 | 16 bit Int | 0.5 | GCP#1 | 1
| TC3 | D/G#2 | EXH. GAS No. 3 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3109 | 16 bit Int | 0.5 | GCP#2 | 1
| TC3 | D/G#3 | EXH. GAS No. 3 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3209 | 16 bit Int | 0.5 | GCP#3 | 1
| TC3 | D/G#4 | EXH. GAS No. 3 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3309 | 16 bit Int | 0.5 | GCP#4 | 1
85 | TC4 | D/G#1 | EXH. GAS No. 4 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3010 | 16 bit Int | 0.5 | GCP#1 | 1
| TC4 | D/G#2 | EXH. GAS No. 4 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3110 | 16 bit Int | 0.5 | GCP#2 | 1
| TC4 | D/G#3 | EXH. GAS No. 4 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3210 | 16 bit Int | 0.5 | GCP#3 | 1
| TC4 | D/G#4 | EXH. GAS No. 4 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3310 | 16 bit Int | 0.5 | GCP#4 | 1
86 | TC5 | D/G#1 | EXH. GAS No. 5 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3011 | 16 bit Int | 0.5 | GCP#1 | 1
| TC5 | D/G#2 | EXH. GAS No. 5 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3111 | 16 bit Int | 0.5 | GCP#2 | 1
| TC5 | D/G#3 | EXH. GAS No. 5 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3211 | 16 bit Int | 0.5 | GCP#3 | 1
| TC5 | D/G#4 | EXH. GAS No. 5 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3311 | 16 bit Int | 0.5 | GCP#4 | 1
87 | TC6 | D/G#1 | EXH. GAS No. 6 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3012 | 16 bit Int | 0.5 | GCP#1 | 1
| TC6 | D/G#2 | EXH. GAS No. 6 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3112 | 16 bit Int | 0.5 | GCP#2 | 1
| TC6 | D/G#3 | EXH. GAS No. 6 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3212 | 16 bit Int | 0.5 | GCP#3 | 1
| TC6 | D/G#4 | EXH. GAS No. 6 CYL, OUT | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3312 | 16 bit Int | 0.5 | GCP#4 | 1
88 | TCTI | D/G#1 | EXH. GAS T/C IN | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3013 | 16 bit Int | 0.5 | GCP#1 | 1
| TCTI | D/G#2 | EXH. GAS T/C IN | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3113 | 16 bit Int | 0.5 | GCP#2 | 1
| TCTI | D/G#3 | EXH. GAS T/C IN | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3213 | 16 bit Int | 0.5 | GCP#3 | 1
| TCTI | D/G#4 | EXH. GAS T/C IN | 0~600°C THERMO-COUPLE K-TYPE JIS C1602 | Analog |  | D3313 | 16 bit Int | 0.5 | GCP#4 | 1
89 | FOT | D/G#1 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | 1 Litre/1 pulse | Analog |  | D3050 D3051 | 32 bit Int | 0.5 | GCP#1 | 1
| FOT | D/G#2 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | 1 Litre/1 pulse | Analog |  | D3150 D3151 | 32 bit Int | 0.5 | GCP#2 | 1
| FOT | D/G#3 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | 1 Litre/1 pulse | Analog |  | D3250 D3251 | 32 bit Int | 0.5 | GCP#3 | 1
| FOT | D/G#4 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | 1 Litre/1 pulse | Analog |  | D3350 D3351 | 32 bit Int | 0.5 | GCP#4 | 1
90 | FOEI | D/G#1 | D.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | D3052 D3053 | 32 bit Int | 0.5 | GCP#1 | 1
| FOEI | D/G#2 | D.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | D3152 D3153 | 32 bit Int | 0.5 | GCP#2 | 1
| FOEI | D/G#3 | D.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | D3252 D3253 | 32 bit Int | 0.5 | GCP#3 | 1
| FOEI | D/G#4 | D.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | D3352 D3353 | 32 bit Int | 0.5 | GCP#4 | 1
91 | FOEO | D/G#1 | D.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | D3054 D3055 | 32 bit Int | 0.5 | GCP#1 | 1
| FOEO | D/G#2 | D.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | D3154 D3155 | 32 bit Int | 0.5 | GCP#2 | 1
| FOEO | D/G#3 | D.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | D3254 D3255 | 32 bit Int | 0.5 | GCP#3 | 1
| FOEO | D/G#4 | D.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | D3354 D3355 | 32 bit Int | 0.5 | GCP#4 | 1
92 | FOHT | D/G#1 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | 1 Litre/1 pulse | Analog |  | D3056 D3057 | 32 bit Int | 0.5 | GCP#1 | 1
| FOHT | D/G#2 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | 1 Litre/1 pulse | Analog |  | D3156 D3157 | 32 bit Int | 0.5 | GCP#2 | 1
| FOHT | D/G#3 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | 1 Litre/1 pulse | Analog |  | D3256 D3257 | 32 bit Int | 0.5 | GCP#3 | 1
| FOHT | D/G#4 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | 1 Litre/1 pulse | Analog |  | D3356 D3357 | 32 bit Int | 0.5 | GCP#4 | 1
93 | FOHEI | D/G#1 | H.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | D3058 D3059 | 32 bit Int | 0.5 | GCP#1 | 1
| FOHEI | D/G#2 | H.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | D3158 D3159 | 32 bit Int | 0.5 | GCP#2 | 1
| FOHEI | D/G#3 | H.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | D3258 D3259 | 32 bit Int | 0.5 | GCP#3 | 1
| FOHEI | D/G#4 | H.O. FLOW METER FOR ENGINE INLET | 1 Litre/1 pulse | Analog |  | D3358 D3359 | 32 bit Int | 0.5 | GCP#4 | 1
94 | FOHEO | D/G#1 | H.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | D3060 D3061 | 32 bit Int | 0.5 | GCP#1 | 1
| FOHEO | D/G#2 | H.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | D3160 D3161 | 32 bit Int | 0.5 | GCP#2 | 1
| FOHEO | D/G#3 | H.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | D3260 D3261 | 32 bit Int | 0.5 | GCP#3 | 1
| FOHEO | D/G#4 | H.O. FLOW METER FOR ENGINE OUTLET | 1 Litre/1 pulse | Analog |  | D3360 D3361 | 32 bit Int | 0.5 | GCP#4 | 1
95 | PTFO | D/G#1 | PRESS. SENSOR FOR FUEL OIL | 0-1.0MPa / 4-20mA | Analog |  | D3014 | 16 bit Int | 0.5 | GCP#1 | 1
| PTFO | D/G#2 | PRESS. SENSOR FOR FUEL OIL | 0-1.0MPa / 4-20mA | Analog |  | D3114 | 16 bit Int | 0.5 | GCP#2 | 1
| PTFO | D/G#3 | PRESS. SENSOR FOR FUEL OIL | 0-1.0MPa / 4-20mA | Analog |  | D3214 | 16 bit Int | 0.5 | GCP#3 | 1
| PTFO | D/G#4 | PRESS. SENSOR FOR FUEL OIL | 0-1.0MPa / 4-20mA | Analog |  | D3314 | 16 bit Int | 0.5 | GCP#4 | 1
96 | PTJW | D/G#1 | PRESS. SENSOR FOR JACKET WATER | 0-0.6MPa / 4-20mA | Analog |  | D3015 | 16 bit Int | 0.5 | GCP#1 | 1
| PTJW | D/G#2 | PRESS. SENSOR FOR JACKET WATER | 0-0.6MPa / 4-20mA | Analog |  | D3115 | 16 bit Int | 0.5 | GCP#2 | 1
| PTJW | D/G#3 | PRESS. SENSOR FOR JACKET WATER | 0-0.6MPa / 4-20mA | Analog |  | D3215 | 16 bit Int | 0.5 | GCP#3 | 1
| PTJW | D/G#4 | PRESS. SENSOR FOR JACKET WATER | 0-0.6MPa / 4-20mA | Analog |  | D3315 | 16 bit Int | 0.5 | GCP#4 | 1
97 | PTCW | D/G#1 | PRESS. SENSOR FOR COOLER WATER | 0-0.6MPa / 4-20mA | Analog |  | D3016 | 16 bit Int | 0.5 | GCP#1 | 1
| PTCW | D/G#2 | PRESS. SENSOR FOR COOLER WATER | 0-0.6MPa / 4-20mA | Analog |  | D3116 | 16 bit Int | 0.5 | GCP#2 | 1
| PTCW | D/G#3 | PRESS. SENSOR FOR COOLER WATER | 0-0.6MPa / 4-20mA | Analog |  | D3216 | 16 bit Int | 0.5 | GCP#3 | 1
| PTCW | D/G#4 | PRESS. SENSOR FOR COOLER WATER | 0-0.6MPa / 4-20mA | Analog |  | D3316 | 16 bit Int | 0.5 | GCP#4 | 1
98 | PTLO | D/G#1 | PRESS. SENSOR FOR ENGINE L.O. | 0-1.0MPa / 4-20mA | Analog |  | D3017 | 16 bit Int | 0.5 | GCP#1 | 1
| PTLO | D/G#2 | PRESS. SENSOR FOR ENGINE L.O. | 0-1.0MPa / 4-20mA | Analog |  | D3117 | 16 bit Int | 0.5 | GCP#2 | 1
| PTLO | D/G#3 | PRESS. SENSOR FOR ENGINE L.O. | 0-1.0MPa / 4-20mA | Analog |  | D3217 | 16 bit Int | 0.5 | GCP#3 | 1
| PTLO | D/G#4 | PRESS. SENSOR FOR ENGINE L.O. | 0-1.0MPa / 4-20mA | Analog |  | D3317 | 16 bit Int | 0.5 | GCP#4 | 1
99 | PTTL0 | D/G#1 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | 0-1.0MPa / 4-20mA | Analog |  | D3018 | 16 bit Int | 0.5 | GCP#1 | 1
| PTTL0 | D/G#2 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | 0-1.0MPa / 4-20mA | Analog |  | D3118 | 16 bit Int | 0.5 | GCP#2 | 1
| PTTL0 | D/G#3 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | 0-1.0MPa / 4-20mA | Analog |  | D3218 | 16 bit Int | 0.5 | GCP#3 | 1
| PTTL0 | D/G#4 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | 0-1.0MPa / 4-20mA | Analog |  | D3318 | 16 bit Int | 0.5 | GCP#4 | 1
100 | PTIA | D/G#1 | PRESS. SENSOR FOR INTAKE-AIR | 0-0.4MPa / 4-20mA | Analog |  | D3019 | 16 bit Int | 0.5 | GCP#1 | 1
| PTIA | D/G#2 | PRESS. SENSOR FOR INTAKE-AIR | 0-0.4MPa / 4-20mA | Analog |  | D3119 | 16 bit Int | 0.5 | GCP#2 | 1
| PTIA | D/G#3 | PRESS. SENSOR FOR INTAKE-AIR | 0-0.4MPa / 4-20mA | Analog |  | D3219 | 16 bit Int | 0.5 | GCP#3 | 1
| PTIA | D/G#4 | PRESS. SENSOR FOR INTAKE-AIR | 0-0.4MPa / 4-20mA | Analog |  | D3319 | 16 bit Int | 0.5 | GCP#4 | 1
101 | 26EX1 | D/G#1 | TURBO-CHARGER GAS OUTLET TEMP. SWITCH (1st) | On over 400°C | Digital |  | M55 | Boolean | 0.5 | GCP#1 | 1 |  | T/C Outlet temperature
| 26EX1 | D/G#2 | TURBO-CHARGER GAS OUTLET TEMP. SWITCH (1st) | On over 400°C | Digital |  | M1055 | Boolean | 0.5 | GCP#2 | 1 |  | T/C Outlet temperature
| 26EX1 | D/G#3 | TURBO-CHARGER GAS OUTLET TEMP. SWITCH (1st) | On over 400°C | Digital |  | M2055 | Boolean | 0.5 | GCP#3 | 1 |  | T/C Outlet temperature
| 26EX1 | D/G#4 | TURBO-CHARGER GAS OUTLET TEMP. SWITCH (1st) | On over 400°C | Digital |  | M3055 | Boolean | 0.5 | GCP#4 | 1 |  | T/C Outlet temperature
102 | TRJWI | D/G#1 | TEMP. SENSOR FOR JACKET WATER INLET | PT100Ω @ 0°C | Analog |  | D3020 | 16 bit Int | 0.5 | GCP#1 | 1
| TRJWI | D/G#2 | TEMP. SENSOR FOR JACKET WATER INLET | PT100Ω @ 0°C | Analog |  | D3120 | 16 bit Int | 0.5 | GCP#2 | 1
| TRJWI | D/G#3 | TEMP. SENSOR FOR JACKET WATER INLET | PT100Ω @ 0°C | Analog |  | D3220 | 16 bit Int | 0.5 | GCP#3 | 1
| TRJWI | D/G#4 | TEMP. SENSOR FOR JACKET WATER INLET | PT100Ω @ 0°C | Analog |  | D3320 | 16 bit Int | 0.5 | GCP#4 | 1
103 | TRJWO | D/G#1 | TEMP. SENSOR FOR JACKET WATER OUTLET | PT100Ω @ 0°C | Analog |  | D3021 | 16 bit Int | 0.5 | GCP#1 | 1
| TRJWO | D/G#2 | TEMP. SENSOR FOR JACKET WATER OUTLET | PT100Ω @ 0°C | Analog |  | D3121 | 16 bit Int | 0.5 | GCP#2 | 1
| TRJWO | D/G#3 | TEMP. SENSOR FOR JACKET WATER OUTLET | PT100Ω @ 0°C | Analog |  | D3221 | 16 bit Int | 0.5 | GCP#3 | 1
| TRJWO | D/G#4 | TEMP. SENSOR FOR JACKET WATER OUTLET | PT100Ω @ 0°C | Analog |  | D3321 | 16 bit Int | 0.5 | GCP#4 | 1
104 | TRCWI | D/G#1 | TEMP. SENSOR FOR COOLER WATER INLET | PT100Ω @ 0°C | Analog |  | D3022 | 16 bit Int | 0.5 | GCP#1 | 1
| TRCWI | D/G#2 | TEMP. SENSOR FOR COOLER WATER INLET | PT100Ω @ 0°C | Analog |  | D3122 | 16 bit Int | 0.5 | GCP#2 | 1
| TRCWI | D/G#3 | TEMP. SENSOR FOR COOLER WATER INLET | PT100Ω @ 0°C | Analog |  | D3222 | 16 bit Int | 0.5 | GCP#3 | 1
| TRCWI | D/G#4 | TEMP. SENSOR FOR COOLER WATER INLET | PT100Ω @ 0°C | Analog |  | D3322 | 16 bit Int | 0.5 | GCP#4 | 1
105 | TRCWO | D/G#1 | TEMP. SENSOR FOR COOLER WATER OUTLET | PT100Ω @ 0°C | Analog |  | D3023 | 16 bit Int | 0.5 | GCP#1 | 1
| TRCWO | D/G#2 | TEMP. SENSOR FOR COOLER WATER OUTLET | PT100Ω @ 0°C | Analog |  | D3123 | 16 bit Int | 0.5 | GCP#2 | 1
| TRCWO | D/G#3 | TEMP. SENSOR FOR COOLER WATER OUTLET | PT100Ω @ 0°C | Analog |  | D3223 | 16 bit Int | 0.5 | GCP#3 | 1
| TRCWO | D/G#4 | TEMP. SENSOR FOR COOLER WATER OUTLET | PT100Ω @ 0°C | Analog |  | D3323 | 16 bit Int | 0.5 | GCP#4 | 1
106 | TRLOI | D/G#1 | TEMP. SENSOR FOR L.O. COOLER INLET | PT100Ω @ 0°C | Analog |  | D3024 | 16 bit Int | 0.5 | GCP#1 | 1
| TRLOI | D/G#2 | TEMP. SENSOR FOR L.O. COOLER INLET | PT100Ω @ 0°C | Analog |  | D3124 | 16 bit Int | 0.5 | GCP#2 | 1
| TRLOI | D/G#3 | TEMP. SENSOR FOR L.O. COOLER INLET | PT100Ω @ 0°C | Analog |  | D3224 | 16 bit Int | 0.5 | GCP#3 | 1
| TRLOI | D/G#4 | TEMP. SENSOR FOR L.O. COOLER INLET | PT100Ω @ 0°C | Analog |  | D3324 | 16 bit Int | 0.5 | GCP#4 | 1
107 | TRLOO | D/G#1 | TEMP. SENSOR FOR L.O. COOLER OUTLET | PT100Ω @ 0°C | Analog |  | D3025 | 16 bit Int | 0.5 | GCP#1 | 1
| TRLOO | D/G#2 | TEMP. SENSOR FOR L.O. COOLER OUTLET | PT100Ω @ 0°C | Analog |  | D3125 | 16 bit Int | 0.5 | GCP#2 | 1
| TRLOO | D/G#3 | TEMP. SENSOR FOR L.O. COOLER OUTLET | PT100Ω @ 0°C | Analog |  | D3225 | 16 bit Int | 0.5 | GCP#3 | 1
| TRLOO | D/G#4 | TEMP. SENSOR FOR L.O. COOLER OUTLET | PT100Ω @ 0°C | Analog |  | D3325 | 16 bit Int | 0.5 | GCP#4 | 1
108 | TRCWB | D/G#1 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | PT100Ω @ 0°C | Analog |  | D3026 | 16 bit Int | 0.5 | GCP#1 | 1
| TRCWB | D/G#2 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | PT100Ω @ 0°C | Analog |  | D3126 | 16 bit Int | 0.5 | GCP#2 | 1
| TRCWB | D/G#3 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | PT100Ω @ 0°C | Analog |  | D3226 | 16 bit Int | 0.5 | GCP#3 | 1
| TRCWB | D/G#4 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | PT100Ω @ 0°C | Analog |  | D3326 | 16 bit Int | 0.5 | GCP#4 | 1
109 | 26F1S | D/G | Thermostat switch for line heater | On below 25oC, Off over 30oC | Digital |  | M4018 | Boolean | 0.5 | GCP | 1
110 | (26F1A) |  | Thermostat switch for line heater | On over 60℃ | Digital |  | M4019 | Boolean |  | GCP | 1
111 | PTSA |  | PRESS SENSOR FOR AIR RECEIVER | 0-5.0MPa / 4-20mA | Analog |  | D3400 | 16 bit Int | 0.5 | GCP#1 | 1
| PTSA |  | PRESS SENSOR FOR AIR RECEIVER | 0-5.0MPa / 4-20mA | Analog |  | D3401 | 16 bit Int | 0.5 | GCP#2 | 1
| PTSA |  | PRESS SENSOR FOR AIR RECEIVER | 0-5.0MPa / 4-20mA | Analog |  | D3402 | 16 bit Int | 0.5 | GCP#3 | 1
112 | 26F2S | D/G | Thermostat sensor for HO Settling tank | On below 60oC, Off over 65oC | Digital |  | M4020 | Boolean | 0.5 | GCP | 1
113 | 26F2A |  | (Thermostat sensor for HO Settling tank heater) | On: above 75oC | Digital |  | M4021 | Boolean |  | GCP | 1 |  | Overheat, heater stop operation
114 | 26F3S |  | Thermostat switch for HO Service tank heater | On below 90oC, Off over 95oC | Digital |  | M4022 | Boolean |  | GCP | 1
115 | 26F4 |  | Thermostat switch for HO Service tank(upper) | On over 90oC, Off below 85oC | Digital |  | M4023 | Boolean |  | GCP | 1
116 | 26F3A |  | (Thermostat switch for HO Service tank heater) | On: above 105oC | Digital |  | M4024 | Boolean |  | GCP | 1 |  | Overheat, heater stop operation
117 | 26F7 |  | Thermostat switch for HO Engine inlet | On below 110oC, Off over 115oC | Digital |  | M4025 | Boolean |  | GCP | 1
118 | 26F8 |  | Thermostat switch for HO Engine inlet | On below 130oC, Off below 125oC | Digital |  | M4026 | Boolean |  | GCP | 1
119 | 63FH |  | Press switch for HO piping | On below 0.5MPa | Digital |  | M4027 | Boolean |  | GCP | 1
120 | 63FD |  | Press switch for DO piping | On below 0.35MPa | Digital |  | M4028 | Boolean |  | GCP | 1
121 | LSDO | D/G#1 | Limit switch for change over valve | On D.O.side | Digital |  | M56 | Boolean | 0.5 | GCP#1 | 1
| LSDO | D/G#1 | Limit switch for change over valve | On D.O.side | Digital |  | M57 | Boolean | 0.5 | GCP#1 | 1
| LSDO | D/G#2 | Limit switch for change over valve | On D.O.side | Digital |  | M1056 | Boolean | 0.5 | GCP#2 | 1
| LSDO | D/G#2 | Limit switch for change over valve | On D.O.side | Digital |  | M1057 | Boolean | 0.5 | GCP#2 | 1
| LSDO | D/G#3 | Limit switch for change over valve | On D.O.side | Digital |  | M2056 | Boolean | 0.5 | GCP#3 | 1
| LSDO | D/G#3 | Limit switch for change over valve | On D.O.side | Digital |  | M2057 | Boolean | 0.5 | GCP#3 | 1
| LSDO | D/G#4 | Limit switch for change over valve | On D.O.side | Digital |  | M3056 | Boolean | 0.5 | GCP#4 | 1
| LSDO | D/G#4 | Limit switch for change over valve | On D.O.side | Digital |  | M3057 | Boolean | 0.5 | GCP#4 | 1
122 | LSHO | D/G#1 | Limit switch for change over valve | On H.O.side | Digital |  | M58 | Boolean | 0.5 | GCP#1 | 1
| LSHO | D/G#1 | Limit switch for change over valve | On H.O.side | Digital |  | M59 | Boolean | 0.5 | GCP#1 | 1
| LSHO | D/G#2 | Limit switch for change over valve | On H.O.side | Digital |  | M1058 | Boolean | 0.5 | GCP#2 | 1
| LSHO | D/G#2 | Limit switch for change over valve | On H.O.side | Digital |  | M1059 | Boolean | 0.5 | GCP#2 | 1
| LSHO | D/G#3 | Limit switch for change over valve | On H.O.side | Digital |  | M2058 | Boolean | 0.5 | GCP#3 | 1
| LSHO | D/G#3 | Limit switch for change over valve | On H.O.side | Digital |  | M2059 | Boolean | 0.5 | GCP#3 | 1
| LSHO | D/G#4 | Limit switch for change over valve | On H.O.side | Digital |  | M3058 | Boolean | 0.5 | GCP#4 | 1
| LSHO | D/G#4 | Limit switch for change over valve | On H.O.side | Digital |  | M3059 | Boolean | 0.5 | GCP#4 | 1
123 | 26F9S |  | Thermostat switch for Drain Tank | On below 50oC, Off below 55oC | Digital |  | M4029 | Boolean |  | GCP | 1
124 | 26F9A |  | (Thermostat switch for Drain Tank Heater) | On: above 65oC | Digital |  | M4030 | Boolean |  | GCP | 1 |  | Overheat, heater stop operation
125 | TRDI | D/G#1 | TEMP. SENSOR for DO Engine inlet | PT100Ω @ 0°C | Analog |  | D3027 | 16 bit Int | 0.5 | GCP#1 | 1
| TRDI | D/G#2 | TEMP. SENSOR for DO Engine inlet | PT100Ω @ 0°C | Analog |  | D3127 | 16 bit Int | 0.5 | GCP#2 | 1
| TRDI | D/G#3 | TEMP. SENSOR for DO Engine inlet | PT100Ω @ 0°C | Analog |  | D3227 | 16 bit Int | 0.5 | GCP#3 | 1
| TRDI | D/G#4 | TEMP. SENSOR for DO Engine inlet | PT100Ω @ 0°C | Analog |  | D3327 | 16 bit Int | 0.5 | GCP#4 | 1
126 | TRDO | D/G#1 | TEMP. SENSOR for DO Engine outlet | PT100Ω @ 0°C | Analog |  | D3028 | 16 bit Int | 0.5 | GCP#1 | 1
| TRDO | D/G#2 | TEMP. SENSOR for DO Engine outlet | PT100Ω @ 0°C | Analog |  | D3128 | 16 bit Int | 0.5 | GCP#2 | 1
| TRDO | D/G#3 | TEMP. SENSOR for DO Engine outlet | PT100Ω @ 0°C | Analog |  | D3228 | 16 bit Int | 0.5 | GCP#3 | 1
| TRDO | D/G#4 | TEMP. SENSOR for DO Engine outlet | PT100Ω @ 0°C | Analog |  | D3328 | 16 bit Int | 0.5 | GCP#4 | 1
127 | TRHI | D/G#1 | TEMP. SENSOR for HO Engine inlet | PT100Ω @ 0°C | Analog |  | D3029 | 16 bit Int | 0.5 | GCP#1 | 1
| TRHI | D/G#2 | TEMP. SENSOR for HO Engine inlet | PT100Ω @ 0°C | Analog |  | D3129 | 16 bit Int | 0.5 | GCP#2 | 1
| TRHI | D/G#3 | TEMP. SENSOR for HO Engine inlet | PT100Ω @ 0°C | Analog |  | D3229 | 16 bit Int | 0.5 | GCP#3 | 1
| TRHI | D/G#4 | TEMP. SENSOR for HO Engine inlet | PT100Ω @ 0°C | Analog |  | D3329 | 16 bit Int | 0.5 | GCP#4 | 1
128 | TRHO | D/G#1 | TEMP. SENSOR for HO Engine outlet | PT100Ω @ 0°C | Analog |  | D3030 | 16 bit Int | 0.5 | GCP#1 | 1
| TRHO | D/G#2 | TEMP. SENSOR for HO Engine outlet | PT100Ω @ 0°C | Analog |  | D3130 | 16 bit Int | 0.5 | GCP#2 | 1
| TRHO | D/G#3 | TEMP. SENSOR for HO Engine outlet | PT100Ω @ 0°C | Analog |  | D3230 | 16 bit Int | 0.5 | GCP#3 | 1
| TRHO | D/G#4 | TEMP. SENSOR for HO Engine outlet | PT100Ω @ 0°C | Analog |  | D3330 | 16 bit Int | 0.5 | GCP#4 | 1
129 |  |  | Viscosity controller | less than 230 CST | Digital |  | M4031 | Boolean | 0.5 |  | 1
130 | TRRA1 | D/G#1 | TEMP. SENSOR FOR RADIATOR 1 | Fault | Digital |  | M60 | Boolean | 0.5 | D/G#1 | 1
| TRRA1 | D/G#2 | TEMP. SENSOR FOR RADIATOR 1 | Fault | Digital |  | M1060 | Boolean | 0.5 | D/G#2 | 1
| TRRA1 | D/G#3 | TEMP. SENSOR FOR RADIATOR 1 | Fault | Digital |  | M2060 | Boolean | 0.5 | D/G#3 | 1
| TRRA1 | D/G#4 | TEMP. SENSOR FOR RADIATOR 1 | Fault | Digital |  | M3060 | Boolean | 0.5 | D/G#4 | 1
131 | TRRA2 | D/G#1 | TEMP. SENSOR FOR RADIATOR 2 | Fault | Digital |  | M61 | Boolean | 0.5 | D/G#1 | 1
| TRRA2 | D/G#2 | TEMP. SENSOR FOR RADIATOR 2 | Fault | Digital |  | M1061 | Boolean | 0.5 | D/G#2 | 1
| TRRA2 | D/G#3 | TEMP. SENSOR FOR RADIATOR 2 | Fault | Digital |  | M2061 | Boolean | 0.5 | D/G#3 | 1
| TRRA2 | D/G#4 | TEMP. SENSOR FOR RADIATOR 2 | Fault | Digital |  | M3061 | Boolean | 0.5 | D/G#4 | 1
132 | TRRA3 | D/G#1 | TEMP. SENSOR FOR RADIATOR 3 | Fault | Digital |  | M62 | Boolean | 0.5 | D/G#1 | 1
| TRRA3 | D/G#2 | TEMP. SENSOR FOR RADIATOR 3 | Fault | Digital |  | M1062 | Boolean | 0.5 | D/G#2 | 1
| TRRA3 | D/G#3 | TEMP. SENSOR FOR RADIATOR 3 | Fault | Digital |  | M2062 | Boolean | 0.5 | D/G#3 | 1
| TRRA3 | D/G#4 | TEMP. SENSOR FOR RADIATOR 3 | Fault | Digital |  | M3062 | Boolean | 0.5 | D/G#4 | 1
133 | TRRA4 | D/G#1 | TEMP. SENSOR FOR RADIATOR 4 | Fault | Digital |  | M63 | Boolean | 0.5 | D/G#1 | 1
| TRRA4 | D/G#2 | TEMP. SENSOR FOR RADIATOR 4 | Fault | Digital |  | M1063 | Boolean | 0.5 | D/G#2 | 1
| TRRA4 | D/G#3 | TEMP. SENSOR FOR RADIATOR 4 | Fault | Digital |  | M2063 | Boolean | 0.5 | D/G#3 | 1
| TRRA4 | D/G#4 | TEMP. SENSOR FOR RADIATOR 4 | Fault | Digital |  | M3063 | Boolean | 0.5 | D/G#4 | 1
134 | HOPF |  | H.O. Purifier Abnormal |  | Digital |  | M4032 | Boolean | 0.5 | GCP | 1
135 | LOPF |  | Lub.Oil Purifier Abnormal |  | Digital |  | M4033 | Boolean | 0.5 | GCP | 1
136 | MD-SX | D/G#1 | OMD ANALOG OUTPUT BOARD |  | Analog |  | D3031 | 16 bit Int | 0.5 | D/G#1 | 1
| MD-SX | D/G#2 | OMD ANALOG OUTPUT BOARD |  | Analog |  | D3131 | 16 bit Int | 0.5 | D/G#2 | 1
| MD-SX | D/G#3 | OMD ANALOG OUTPUT BOARD |  | Analog |  | D3231 | 16 bit Int | 0.5 | D/G#3 | 1
| MD-SX | D/G#4 | OMD ANALOG OUTPUT BOARD |  | Analog |  | D3331 | 16 bit Int | 0.5 | D/G#4 | 1
137 | 33SD |  | Level Switch for Sludge Tank |  | Digital |  | M4034 | Boolean |  | GCP | 1
140 |  | D/G#1 | Voltage [Generator] | V | Analog |  | D3032 | 16 bit Int | 0.5 | GCP#1 | 1
|  | D/G#2 | Voltage [Generator] | V | Analog |  | D3132 | 16 bit Int | 0.5 | GCP#2 | 1
|  | D/G#3 | Voltage [Generator] | V | Analog |  | D3232 | 16 bit Int | 0.5 | GCP#3 | 1
|  | D/G#4 | Voltage [Generator] | V | Analog |  | D3332 | 16 bit Int | 0.5 | GCP#4 | 1
141 |  | D/G#1 | Frequency [Generator] | Hz | Analog |  | D3033 | 16 bit Int | 0.5 | GCP#1 | 1
|  | D/G#2 | Frequency [Generator] | Hz | Analog |  | D3133 | 16 bit Int | 0.5 | GCP#2 | 1
|  | D/G#3 | Frequency [Generator] | Hz | Analog |  | D3233 | 16 bit Int | 0.5 | GCP#3 | 1
|  | D/G#4 | Frequency [Generator] | Hz | Analog |  | D3333 | 16 bit Int | 0.5 | GCP#4 | 1
141A |  | D/G#1 | Power Factor [Generator] |  | Analog |  | D3034 | 16 bit Int | 0.5 | GCP#1 | 1
|  | D/G#2 | Power Factor [Generator] |  | Analog |  | D3134 | 16 bit Int | 0.5 | GCP#2 | 1
|  | D/G#3 | Power Factor [Generator] |  | Analog |  | D3234 | 16 bit Int | 0.5 | GCP#3 | 1
|  | D/G#4 | Power Factor [Generator] |  | Analog |  | D3334 | 16 bit Int | 0.5 | GCP#4 | 1
142 | 52G1 |  | VCB Status [Generator][52G1] | Close | Digital |  | M64 | Boolean | 0.5 | GCP#1 | 1
|  |  |  | Open | Digital |  | M65 | Boolean | 0.5 | GCP#1 | 1
|  |  |  | Fault (Non-close)/trip | Digital |  | M66 | Boolean | 0.5 | GCP#1 | 1
| 52G2 |  | VCB Status [Generator][52G1] | Close | Digital |  | M1064 | Boolean | 0.5 | GCP#2 | 1
|  |  |  | Open | Digital |  | M1065 | Boolean | 0.5 | GCP#2 | 1
|  |  |  | Fault (Non-close)/trip | Digital |  | M1066 | Boolean | 0.5 | GCP#2 | 1
| 52G3 |  | VCB Status [Generator][52G1] | Close | Digital |  | M2064 | Boolean | 0.5 | GCP#3 | 1
|  |  |  | Open | Digital |  | M2065 | Boolean | 0.5 | GCP#3 | 1
|  |  |  | Fault (Non-close)/trip | Digital |  | M2066 | Boolean | 0.5 | GCP#3 | 1
| 52G4 |  | VCB Status [Generator][52G1] | Close | Digital |  | M3064 | Boolean | 0.5 | GCP#4 | 1
|  |  |  | Open | Digital |  | M3065 | Boolean | 0.5 | GCP#4 | 1
|  |  |  | Fault (Non-close)/trip | Digital |  | M3066 | Boolean | 0.5 | GCP#4 | 1
143 |  | D/G#1 | Current [Generator] | Amphere | Analog |  | D3035 | 16 bit Int | 0.5 | GCP#1 | 1
|  | D/G#2 | Current [Generator] | Amphere | Analog |  | D3135 | 16 bit Int | 0.5 | GCP#2 | 1
|  | D/G#3 | Current [Generator] | Amphere | Analog |  | D3235 | 16 bit Int | 0.5 | GCP#3 | 1
|  | D/G#4 | Current [Generator] | Amphere | Analog |  | D3335 | 16 bit Int | 0.5 | GCP#4 | 1
144 |  | D/G#1 | Running hours [Generator] | hrs | Analog |  | D3036 | 16 bit Int | 0.5 | GCP#1 | 1
|  | D/G#2 | Running hours [Generator] | hrs | Analog |  | D3136 | 16 bit Int | 0.5 | GCP#2 | 1
|  | D/G#3 | Running hours [Generator] | hrs | Analog |  | D3236 | 16 bit Int | 0.5 | GCP#3 | 1
|  | D/G#4 | Running hours [Generator] | hrs | Analog |  | D3336 | 16 bit Int | 0.5 | GCP#4 | 1
145 |  | D/G#1 | Rack Reading | mm | Analog |  |  |  | 0.5 | GCP#1 | 1
|  | D/G#2 | Rack Reading | mm | Analog |  |  |  | 0.5 | GCP#2 | 1
|  | D/G#3 | Rack Reading | mm | Analog |  |  |  | 0.5 | GCP#3 | 1
|  | D/G#4 | Rack Reading | mm | Analog |  |  |  | 0.5 | GCP#4 | 1
146 |  | D/G#1 | Power [Generator] | kWe | Analog |  | D3037 | 16 bit Int | 0.5 | GCP#1 | 1
|  | D/G#2 | Power [Generator] | kWe | Analog |  | D3137 | 16 bit Int | 0.5 | GCP#2 | 1
|  | D/G#3 | Power [Generator] | kWe | Analog |  | D3237 | 16 bit Int | 0.5 | GCP#3 | 1
|  | D/G#4 | Power [Generator] | kWe | Analog |  | D3337 | 16 bit Int | 0.5 | GCP#4 | 1
147 |  | D/G#1 | Engine RPM | min-1 | Analog |  | D3038 | 16 bit Int | 0.5 | GCP#1 | 1
|  | D/G#2 | Engine RPM | min-1 | Analog |  | D3138 | 16 bit Int | 0.5 | GCP#2 | 1
|  | D/G#3 | Engine RPM | min-1 | Analog |  | D3238 | 16 bit Int | 0.5 | GCP#3 | 1
|  | D/G#4 | Engine RPM | min-1 | Analog |  | D3338 | 16 bit Int | 0.5 | GCP#4 | 1
154 |  | D/G#1 | Ready to start |  | Digital |  | M67 | Boolean | 0.5 | GCP#1 | 1
|  | D/G#2 | Ready to start |  | Digital |  | M1067 | Boolean | 0.5 | GCP#2 | 1
|  | D/G#3 | Ready to start |  | Digital |  | M2067 | Boolean | 0.5 | GCP#3 | 1
|  | D/G#4 | Ready to start |  | Digital |  | M3067 | Boolean | 0.5 | GCP#4 | 1
155 | IM1 |  | No.1 Turning Motor | Abnormal trip | Digital |  | M68 | Boolean |  | GCP#1 | 1
|  |  |  | FWD Running | Digital |  | M69 | Boolean |  | GCP#1 | 1
|  |  |  | Rev Running | Digital |  | M70 | Boolean |  | GCP#1 | 1
|  |  |  | Remote mode | Digital |  | M71 | Boolean |  | GCP#1 | 1
|  |  | No.2 Turning Motor | Abnormal trip | Digital |  | M1068 | Boolean |  | GCP#2 | 1
|  |  |  | FWD Running | Digital |  | M1069 | Boolean |  | GCP#2 | 1
|  |  |  | Rev Running | Digital |  | M1070 | Boolean |  | GCP#2 | 1
|  |  |  | Remote mode | Digital |  | M1071 | Boolean |  | GCP#2 | 1
|  |  | No.3 Turning Motor | Abnormal trip | Digital |  | M2068 | Boolean |  | GCP#3 | 1
|  |  |  | FWD Running | Digital |  | M2069 | Boolean |  | GCP#3 | 1
|  |  |  | Rev Running | Digital |  | M2070 | Boolean |  | GCP#3 | 1
|  |  |  | Remote mode | Digital |  | M2071 | Boolean |  | GCP#3 | 1
|  |  | No.4 Turning Motor | Abnormal trip | Digital |  | M3068 | Boolean |  | GCP#4 | 1
|  |  |  | FWD Running | Digital |  | M3069 | Boolean |  | GCP#4 | 1
|  |  |  | Rev Running | Digital |  | M3070 | Boolean |  | GCP#4 | 1
|  |  |  | Remote mode | Digital |  | M3071 | Boolean |  | GCP#4 | 1
156 | IM2 |  | No.1 LO Priming Pump Motor status | Auto start [GCP] | Digital |  | M72 | Boolean |  | GCP#1 | 1
|  |  |  | Auto Stop {GCP] | Digital |  | M73 | Boolean |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  | M74 | Boolean |  | GCP#1 | 1
|  |  |  | Running | Digital |  | M75 | Boolean |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  | M76 | Boolean |  | GCP#1 | 1
|  |  |  | Remote start [LCP] | Digital |  | M77 | Boolean |  | GCP#1 | 1
|  |  |  | Remote Stop [LCP] | Digital |  | M78 | Boolean |  | GCP#1 | 1
|  |  | No.2 LO Priming Pump Motor status | Auto start [GCP] | Digital |  | M1072 | Boolean |  | GCP#2 | 1
|  |  |  | Auto Stop {GCP] | Digital |  | M1073 | Boolean |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  | M1074 | Boolean |  | GCP#2 | 1
|  |  |  | Running | Digital |  | M1075 | Boolean |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  | M1076 | Boolean |  | GCP#2 | 1
|  |  |  | Remote start [LCP] | Digital |  | M1077 | Boolean |  | GCP#2 | 1
|  |  |  | Remote Stop [LCP] | Digital |  | M1078 | Boolean |  | GCP#2 | 1
|  |  | No.3 LO Priming Pump Motor status | Auto start [GCP] | Digital |  | M2072 | Boolean |  | GCP#3 | 1
|  |  |  | Auto Stop {GCP] | Digital |  | M2073 | Boolean |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  | M2074 | Boolean |  | GCP#3 | 1
|  |  |  | Running | Digital |  | M2075 | Boolean |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  | M2076 | Boolean |  | GCP#3 | 1
|  |  |  | Remote start [LCP] | Digital |  | M2077 | Boolean |  | GCP#3 | 1
|  |  |  | Remote Stop [LCP] | Digital |  | M2078 | Boolean |  | GCP#3 | 1
|  |  | No.4 LO Priming Pump Motor status | Auto start [GCP] | Digital |  | M3072 | Boolean |  | GCP#4 | 1
|  |  |  | Auto Stop {GCP] | Digital |  | M3073 | Boolean |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  | M3074 | Boolean |  | GCP#4 | 1
|  |  |  | Running | Digital |  | M3075 | Boolean |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  | M3076 | Boolean |  | GCP#4 | 1
|  |  |  | Remote start [LCP] | Digital |  | M3077 | Boolean |  | GCP#4 | 1
|  |  |  | Remote Stop [LCP] | Digital |  | M3078 | Boolean |  | GCP#4 | 1
157 | IM3 |  | No.1 Air Compressor status | Auto start [GCP] | Digital |  | M4035 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4036 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4037 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4038 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4039 | Boolean |  | GCP | 1
|  |  | No.2 Air Compressor status | Auto start [GCP] | Digital |  | M4040 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4041 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4042 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4043 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4044 | Boolean |  | GCP | 1
158 | IM4 |  | No.1 Mist Fan | Auto start [GCP] | Digital |  | M79 | Boolean |  | GCP#1 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M80 | Boolean |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  | M81 | Boolean |  | GCP#1 | 1
|  |  |  | Running | Digital |  | M82 | Boolean |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  | M83 | Boolean |  | GCP#1 | 1
|  |  | No.2 Mist Fan | Auto start [GCP] | Digital |  | M1079 | Boolean |  | GCP#2 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M1080 | Boolean |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  | M1081 | Boolean |  | GCP#2 | 1
|  |  |  | Running | Digital |  | M1082 | Boolean |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  | M1083 | Boolean |  | GCP#2 | 1
|  |  | No.3 Mist Fan | Auto start [GCP] | Digital |  | M2079 | Boolean |  | GCP#3 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M2080 | Boolean |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  | M2081 | Boolean |  | GCP#3 | 1
|  |  |  | Running | Digital |  | M2082 | Boolean |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  | M2083 | Boolean |  | GCP#3 | 1
|  |  | No.4 Mist Fan | Auto start [GCP] | Digital |  | M3079 | Boolean |  | GCP#4 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M3080 | Boolean |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  | M3081 | Boolean |  | GCP#4 | 1
|  |  |  | Running | Digital |  | M3082 | Boolean |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  | M3083 | Boolean |  | GCP#4 | 1
159 | IM5 |  | No.1 DO Transfer Pump | Auto start [GCP] | Digital |  | M4045 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4046 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4047 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4048 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4049 | Boolean |  | GCP | 1
|  |  | No.2 DO Transfer Pump | Auto start [GCP] | Digital |  | M4050 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4051 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4052 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4053 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4054 | Boolean |  | GCP | 1
160 | IM6 |  | No.1 DO Feed Pump | Auto start [GCP] | Digital |  | M4055 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4056 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4057 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4058 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4059 | Boolean |  | GCP | 1
|  |  | No.2 DO Feed Pump | Auto start [GCP] | Digital |  | M4060 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4061 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4062 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4063 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4064 | Boolean |  | GCP | 1
161 | IM7 |  | No.1 HO Transfer Pump | Auto start [GCP] | Digital |  | M4065 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4066 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4067 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4068 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4069 | Boolean |  | GCP | 1
|  |  | No.2 HO Transfer Pump | Auto start [GCP] | Digital |  | M4070 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4071 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4072 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4073 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4074 | Boolean |  | GCP | 1
162 | IM8 |  | No.1 HO Pressure Pump | Auto start [GCP] | Digital |  | M4075 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4076 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4077 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4078 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4079 | Boolean |  | GCP | 1
|  |  | No.2 HO Pressure Pump | Auto start [GCP] | Digital |  | M4080 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4081 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4082 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4083 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4084 | Boolean |  | GCP | 1
163 | IM9 |  | No.1 HO Feed Pump | Auto start [GCP] | Digital |  | M4085 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4086 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4087 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4088 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4089 | Boolean |  | GCP | 1
|  |  | No.2 HO Feed Pump | Auto start [GCP] | Digital |  | M4090 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4091 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4092 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4093 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4094 | Boolean |  | GCP | 1
164 | IM10 |  | No.1 FO Drain Pump | Auto start [GCP] | Digital |  | M4095 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4096 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4097 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4098 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4099 | Boolean |  | GCP | 1
|  |  | No.2 FO Drain Pump | Auto start [GCP] | Digital |  | M4100 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4101 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4102 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4103 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4104 | Boolean |  | GCP | 1
165 | IM11 |  | No.1 DO/HO change over valve [Engine inlet] | Energize | Digital |  | M84 | Boolean |  | GCP#1 | 1
|  |  |  | De-energize | Digital |  | M85 | Boolean |  | GCP#1 | 1
|  |  | No.2 DO/HO change over valve [Engine inlet] | Energize | Digital |  | M1084 | Boolean |  | GCP#2 | 1
|  |  |  | De-energize | Digital |  | M1085 | Boolean |  | GCP#2 | 1
|  |  | No.3 DO/HO change over valve [Engine inlet] | Energize | Digital |  | M2084 | Boolean |  | GCP#3 | 1
|  |  |  | De-energize | Digital |  | M2085 | Boolean |  | GCP#3 | 1
|  |  | No.4 DO/HO change over valve [Engine inlet] | Energize | Digital |  | M3084 | Boolean |  | GCP#4 | 1
|  |  |  | De-energize | Digital |  | M3085 | Boolean |  | GCP#4 | 1
|  |  | No.1 DO/HO change over valve [Engine outlet] | Energize | Digital |  | M86 | Boolean |  | GCP#1 | 1
|  |  |  | De-energize | Digital |  | M87 | Boolean |  | GCP#1 | 1
|  |  | No.2 DO/HO change over valve [Engine outlet] | Energize | Digital |  | M1086 | Boolean |  | GCP#2 | 1
|  |  |  | De-energize | Digital |  | M1087 | Boolean |  | GCP#2 | 1
|  |  | No.3 DO/HO change over valve [Engine outlet] | Energize | Digital |  | M2086 | Boolean |  | GCP#3 | 1
|  |  |  | De-energize | Digital |  | M2087 | Boolean |  | GCP#3 | 1
|  |  | No.4 DO/HO change over valve [Engine outlet] | Energize | Digital |  | M3086 | Boolean |  | GCP#4 | 1
|  |  |  | De-energize | Digital |  | M3087 | Boolean |  | GCP#4 | 1
166 | IM12 |  | No.1 Inlet Fan | Auto start [GCP] | Digital |  | M4105 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4106 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4107 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4108 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4109 | Boolean |  | GCP | 1
|  |  | No.2 Inlet Fan | Auto start [GCP] | Digital |  | M4110 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4111 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4112 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4113 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4114 | Boolean |  | GCP | 1
|  |  | No.3 Inlet Fan | Auto start [GCP] | Digital |  | M4115 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4116 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4117 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4118 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4119 | Boolean |  | GCP | 1
|  |  | No.4 Inlet Fan | Auto start [GCP] | Digital |  | M4120 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4121 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4122 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4123 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4124 | Boolean |  | GCP | 1
|  |  | No.5 Inlet Fan | Auto start [GCP] | Digital |  | M4125 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4126 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4127 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4128 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4129 | Boolean |  | GCP | 1
167 | IM13 |  | No.1 Outlet Fan | Auto start [GCP] | Digital |  | M4130 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4131 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4132 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4133 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4134 | Boolean |  | GCP | 1
|  |  | No.2 Outlet Fan | Auto start [GCP] | Digital |  | M4135 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4136 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4137 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4138 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4139 | Boolean |  | GCP | 1
|  |  | No.3 Outlet Fan | Auto start [GCP] | Digital |  | M4140 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4141 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4142 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4143 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4144 | Boolean |  | GCP | 1
|  |  | No.4 Outlet Fan | Auto start [GCP] | Digital |  | M4145 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4146 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4147 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4148 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4149 | Boolean |  | GCP | 1
|  |  | No.5 Outlet Fan | Auto start [GCP] | Digital |  | M4150 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4151 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4152 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4153 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4154 | Boolean |  | GCP | 1
168 | IM14 |  | Overhead crane | Abnormal trip | Digital |  | M4155 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4156 | Boolean |  | GCP | 1
169 | IM15 |  | Air conditioner | Fault | Digital |  | M4157 | Boolean |  | GCP | 1
170 | IM16 |  | Viscosity controller | Fault | Digital |  | M4158 | Boolean |  | GCP | 1
171 | IM29 |  | L.O makeup Pump | Abnormal trip | Digital |  | M4159 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4160 | Boolean |  | GCP | 1
172 | IM19 |  | No.1 Alternator Space heater | Auto start [GCP] | Digital |  | M88 | Boolean |  | GCP#1 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M89 | Boolean |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  | M90 | Boolean |  | GCP#1 | 1
|  |  |  | Running | Digital |  | M91 | Boolean |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  | M92 | Boolean |  | GCP#1 | 1
|  |  | No.2 Alternator Space heater | Auto start [GCP] | Digital |  | M1088 | Boolean |  | GCP#2 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M1089 | Boolean |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  | M1090 | Boolean |  | GCP#2 | 1
|  |  |  | Running | Digital |  | M1091 | Boolean |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  | M1092 | Boolean |  | GCP#2 | 1
|  |  | No.3 Alternator Space heater | Auto start [GCP] | Digital |  | M2088 | Boolean |  | GCP#3 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M2089 | Boolean |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  | M2090 | Boolean |  | GCP#3 | 1
|  |  |  | Running | Digital |  | M2091 | Boolean |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  | M2092 | Boolean |  | GCP#3 | 1
|  |  | No.4 Alternator Space heater | Auto start [GCP] | Digital |  | M3088 | Boolean |  | GCP#4 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M3089 | Boolean |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  | M3090 | Boolean |  | GCP#4 | 1
|  |  |  | Running | Digital |  | M3091 | Boolean |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  | M3092 | Boolean |  | GCP#4 | 1
173 | IM39 |  | DO unloading pump | Abnormal trip | Digital |  | M4161 | Boolean |  | GCP | 1 |  | LCBD: Start, Stop Push button [manual]
|  |  |  | Running | Digital |  | M4162 | Boolean |  | GCP | 1
174 | IM 22 |  | HO unloading pump | Abnormal trip | Digital |  | M4163 | Boolean |  | GCP | 1 |  | LCBH: Start, Stop Push button [manual]
|  |  |  | Running | Digital |  | M4164 | Boolean |  | GCP | 1
175 | IM18 |  | Inline heater | Auto start [GCP] | Digital |  | M4165 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4166 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4167 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4168 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4169 | Boolean |  | GCP | 1
176 | IM23 |  | HO settling tank heater | Auto start [GCP] | Digital |  | M4170 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4171 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4172 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4173 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4174 | Boolean |  | GCP | 1
177 | IM24 |  | No.1 HO purifier Heater | Fault | Digital |  | M4175 | Boolean |  | GCP | 1
|  |  | No.2 HO purifier Heater | Fault | Digital |  | M4176 | Boolean |  | GCP | 1
178 | IM25 |  | No.1 HO purifier Pump | Abnormal trip | Digital |  | M4177 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4178 | Boolean |  | GCP | 1
|  |  | No.1 HO purifier Pump | Abnormal trip | Digital |  | M4179 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4180 | Boolean |  | GCP | 1
179 | IM27 |  | No.1 HO service tank heater | Auto start [GCP] | Digital |  | M4181 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4182 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4183 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4184 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4185 | Boolean |  | GCP | 1
|  |  | No.2 HO service tank heater | Auto start [GCP] | Digital |  | M4186 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4187 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4188 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4189 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4190 | Boolean |  | GCP | 1
180 | IM17 |  | HO line heater | Fault | Digital |  | M4191 | Boolean |  | GCP | 1
181 | IM28 |  | HO back wash filter | Fault | Digital |  | M4192 | Boolean |  | GCP | 1
182 | IM30 |  | No.1 F.O drain tank heater | Auto start [GCP] | Digital |  | M4193 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4194 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4195 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4196 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4197 | Boolean |  | GCP | 1
|  |  | No.2 F.O drain tank heater | Auto start [GCP] | Digital |  | M4198 | Boolean |  | GCP | 1 |  | As per the customer, there's 02 drain pump, maoybe 01 not in use?
|  |  |  | Auto Stop [GCP] | Digital |  | M4199 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4200 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4201 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4202 | Boolean |  | GCP | 1
183 | IM26 |  | No.1 HT Radiator Fan Motor | Auto start [GCP] | Digital |  | M93 | Boolean |  | GCP#1 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M94 | Boolean |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  | M95 | Boolean |  | GCP#1 | 1
|  |  |  | Running | Digital |  | M96 | Boolean |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  | M97 | Boolean |  | GCP#1 | 1
|  |  | No.2 HT Radiator Fan Motor | Auto start [GCP] | Digital |  | M1093 | Boolean |  | GCP#2 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M1094 | Boolean |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  | M1095 | Boolean |  | GCP#2 | 1
|  |  |  | Running | Digital |  | M1096 | Boolean |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  | M1097 | Boolean |  | GCP#2 | 1
|  |  | No.3 HT Radiator Fan Motor | Auto start [GCP] | Digital |  | M2093 | Boolean |  | GCP#3 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M2094 | Boolean |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  | M2095 | Boolean |  | GCP#3 | 1
|  |  |  | Running | Digital |  | M2096 | Boolean |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  | M2097 | Boolean |  | GCP#3 | 1
|  |  | No.4 HT Radiator Fan Motor | Auto start [GCP] | Digital |  | M3093 | Boolean |  | GCP#4 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M3094 | Boolean |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  | M3095 | Boolean |  | GCP#4 | 1
|  |  |  | Running | Digital |  | M3096 | Boolean |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  | M3097 | Boolean |  | GCP#4 | 1
184 | IM38 |  | No.1 LT Radiator Fan Motor | Auto start [GCP] | Digital |  | M98 | Boolean |  | GCP#1 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M99 | Boolean |  | GCP#1 | 1
|  |  |  | Abnormal trip | Digital |  | M100 | Boolean |  | GCP#1 | 1
|  |  |  | Running | Digital |  | M101 | Boolean |  | GCP#1 | 1
|  |  |  | Auto mode | Digital |  | M102 | Boolean |  | GCP#1 | 1
|  |  | No.2 LT Radiator Fan Motor | Auto start [GCP] | Digital |  | M1098 | Boolean |  | GCP#2 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M1099 | Boolean |  | GCP#2 | 1
|  |  |  | Abnormal trip | Digital |  | M1100 | Boolean |  | GCP#2 | 1
|  |  |  | Running | Digital |  | M1101 | Boolean |  | GCP#2 | 1
|  |  |  | Auto mode | Digital |  | M1102 | Boolean |  | GCP#2 | 1
|  |  | No.3 LT Radiator Fan Motor | Auto start [GCP] | Digital |  | M2098 | Boolean |  | GCP#3 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M2099 | Boolean |  | GCP#3 | 1
|  |  |  | Abnormal trip | Digital |  | M2100 | Boolean |  | GCP#3 | 1
|  |  |  | Running | Digital |  | M2101 | Boolean |  | GCP#3 | 1
|  |  |  | Auto mode | Digital |  | M2102 | Boolean |  | GCP#3 | 1
|  |  | No.4 LT Radiator Fan Motor | Auto start [GCP] | Digital |  | M3098 | Boolean |  | GCP#4 | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M3099 | Boolean |  | GCP#4 | 1
|  |  |  | Abnormal trip | Digital |  | M3100 | Boolean |  | GCP#4 | 1
|  |  |  | Running | Digital |  | M3101 | Boolean |  | GCP#4 | 1
|  |  |  | Auto mode | Digital |  | M3102 | Boolean |  | GCP#4 | 1
185 | IM31 |  | Drain discharge pump | Abnormal trip | Digital |  | M4203 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4204 | Boolean |  | GCP | 1
186 | IM32 |  | Make up water pump | Abnormal trip | Digital |  | M4205 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4206 | Boolean |  | GCP | 1
187 | IM20 |  | No.1 LO purifier heater | Abnormal trip | Digital |  | M4207 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4208 | Boolean |  | GCP | 1
|  |  | No.2 LO purifier heater | Abnormal trip | Digital |  | M4209 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4210 | Boolean |  | GCP | 1
|  |  | No.3 LO purifier heater | Abnormal trip | Digital |  | M4211 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4212 | Boolean |  | GCP | 1
|  |  | No.4 LO purifier heater | Abnormal trip | Digital |  | M4213 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4214 | Boolean |  | GCP | 1
188 | IM21 |  | No.1 LO purifier pump | Abnormal trip | Digital |  | M4215 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4216 | Boolean |  | GCP | 1
|  |  | No.2 LO purifier pump | Abnormal trip | Digital |  | M4217 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4218 | Boolean |  | GCP | 1
|  |  | No.3 LO purifier pump | Abnormal trip | Digital |  | M4219 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4220 | Boolean |  | GCP | 1
|  |  | No.4 LO purifier pump | Abnormal trip | Digital |  | M4221 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4222 | Boolean |  | GCP | 1
189 | IM34 |  | Sludge transfer pump | Auto start [GCP] | Digital |  | M4223 | Boolean |  | GCP | 1 |  | LCBS: Start, Stop Push button [manual]
|  |  |  | Auto Stop [GCP] | Digital |  | M4224 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4225 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4226 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4227 | Boolean |  | GCP | 1
|  |  | Spare | Auto start [GCP] | Digital |  | M4228 | Boolean |  | GCP | 1
|  |  |  | Auto Stop [GCP] | Digital |  | M4229 | Boolean |  | GCP | 1
|  |  |  | Abnormal trip | Digital |  | M4230 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4231 | Boolean |  | GCP | 1
|  |  |  | Auto mode | Digital |  | M4232 | Boolean |  | GCP | 1
190 | IM35 |  | No.1 Oily water drain pump | Abnormal trip | Digital |  | M4233 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4234 | Boolean |  | GCP | 1
|  |  | No.2 Oily water drain pump | Abnormal trip | Digital |  | M4235 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4236 | Boolean |  | GCP | 1
191 | IM33 |  | Water supply pump | Abnormal trip | Digital |  | M4237 | Boolean |  | GCP | 1
|  |  |  | Running | Digital |  | M4238 | Boolean |  | GCP | 1
192 | IM37 |  | Lighting for Engine room | Fault | Digital |  | M4239 | Boolean |  | GCP | 1
193 |  |  | Control Panel | Fault | Digital |  | M4240 | Boolean |  | GCP | 1
194 |  |  | No.1 OMD | Fault | Digital |  | M4241 | Boolean |  | GCP | 1
|  |  | No.2 OMD | Fault | Digital |  | M4242 | Boolean |  | GCP | 1
|  |  | No.3 OMD | Fault | Digital |  | M4243 | Boolean |  | GCP | 1
|  |  | No.4 OMD | Fault | Digital |  | M4244 | Boolean |  | GCP | 1
195 |  |  | Heat trace No.1 | Fault | Digital |  | M4245 | Boolean |  | GCP | 1
|  |  | Heat trace No.2 | Fault | Digital |  | M4246 | Boolean |  | GCP | 1
|  |  | Heat trace No.3 | Fault | Digital |  | M4247 | Boolean |  | GCP | 1
|  |  | Heat trace No.4 | Fault | Digital |  | M4248 | Boolean |  | GCP | 1
|  |  | Heat trace No.5 | Fault | Digital |  | M4249 | Boolean |  | GCP | 1
|  |  | Heat trace No.6 | Fault | Digital |  | M4250 | Boolean |  | GCP | 1
|  |  | Heat trace No.7 | Fault | Digital |  | M4251 | Boolean |  | GCP | 1
|  |  | Heat trace No.8 | Fault | Digital |  | M4252 | Boolean |  | GCP | 1
|  |  | Heat trace No.9 | Fault | Digital |  | M4253 | Boolean |  | GCP | 1
|  |  | Heat trace No.10 | Fault | Digital |  | M4254 | Boolean |  | GCP | 1
|  |  | Heat trace No.11 | Fault | Digital |  | M4255 | Boolean |  | GCP | 1
|  |  | Heat trace No.12 | Fault | Digital |  | M4256 | Boolean |  | GCP | 1
|  |  | Heat trace No.13 | Fault | Digital |  | M4257 | Boolean |  | GCP | 1
|  |  | Heat trace No.14 | Fault | Digital |  | M4258 | Boolean |  | GCP | 1
|  |  | Heat trace No.15 | Fault | Digital |  | M4259 | Boolean |  | GCP | 1
|  |  | Heat trace No.16 | Fault | Digital |  | M4260 | Boolean |  | GCP | 1
|  |  | Heat trace No.17 | Fault | Digital |  | M4261 | Boolean |  | GCP | 1
|  |  | Heat trace No.18 | Fault | Digital |  | M4262 | Boolean |  | GCP | 1
|  |  | Heat trace No.19 | Fault | Digital |  | M4263 | Boolean |  | GCP | 1
|  |  | Heat trace No.20 | Fault | Digital |  | M4264 | Boolean |  | GCP | 1
|  |  | Heat trace No.21 | Fault | Digital |  | M4265 | Boolean |  | GCP | 1
|  |  | Heat trace No.22 | Fault | Digital |  | M4266 | Boolean |  | GCP | 1
|  |  | Heat trace No.23 | Fault | Digital |  | M4267 | Boolean |  | GCP | 1
|  |  | Heat trace No.24 | Fault | Digital |  | M4268 | Boolean |  | GCP | 1
196 |  |  | Drums | Fault | Digital |  |  |  |  | GCP | 1 |  | DRUMS will provide fault dry contacts for DC Supply 1 and DC Supply 2 for its redundant power supply modules and there will be "No GCP connection fault" dry contact as well.
197 | 50,51 | D/G#1 | VCB TRIP(50,51,51N,86,59,27,87G,40,32R,46,81) |  |  |  | M103 | Boolean | 0.5 | GCP#1 | 1
| 50,51 | D/G#2 | VCB TRIP(50,51,51N,86,59,27,87G,40,32R,46,81) |  |  |  | M1103 | Boolean | 0.5 | GCP#2 | 1
| 50,51 | D/G#3 | VCB TRIP(50,51,51N,86,59,27,87G,40,32R,46,81) |  |  |  | M2103 | Boolean | 0.5 | GCP#3 | 1
| 50,51 | D/G#4 | VCB TRIP(50,51,51N,86,59,27,87G,40,32R,46,81) |  |  |  | M3103 | Boolean | 0.5 | GCP#4 | 1
202 | 59 | D/G#1 | Over Voltage | [5 empty] | 0.5 | GCP#1 | 1
| 59 | D/G#2 | Over Voltage | [5 empty] | 0.5 | GCP#2 | 1
| 59 | D/G#3 | Over Voltage | [5 empty] | 0.5 | GCP#3 | 1
| 59 | D/G#4 | Over Voltage | [5 empty] | 0.5 | GCP#4 | 1
203 | 51N | D/G#1 | Earth Fault | [5 empty] | 0.5 | GCP#1 | 1
| 51N | D/G#2 | Earth Fault | [5 empty] | 0.5 | GCP#2 | 1
| 51N | D/G#3 | Earth Fault | [5 empty] | 0.5 | GCP#3 | 1
| 51N | D/G#4 | Earth Fault | [5 empty] | 0.5 | GCP#4 | 1
204 | 27 | D/G#1 | Under Voltage | [5 empty] | 0.5 | GCP#1 | 1
| 27 | D/G#2 | Under Voltage | [5 empty] | 0.5 | GCP#2 | 1
| 27 | D/G#3 | Under Voltage | [5 empty] | 0.5 | GCP#3 | 1
| 27 | D/G#4 | Under Voltage | [5 empty] | 0.5 | GCP#4 | 1
205 | 87G | D/G#1 | Diff Protection | [5 empty] | 0.5 | GCP#1 | 1
| 87G | D/G#2 | Diff Protection | [5 empty] | 0.5 | GCP#2 | 1
| 87G | D/G#3 | Diff Protection | [5 empty] | 0.5 | GCP#3 | 1
| 87G | D/G#4 | Diff Protection | [5 empty] | 0.5 | GCP#4 | 1
206 | 40 | D/G#1 | Under Excitation | [5 empty] | 0.5 | GCP#1 | 1
| 40 | D/G#2 | Under Excitation | [5 empty] | 0.5 | GCP#2 | 1
| 40 | D/G#3 | Under Excitation | [5 empty] | 0.5 | GCP#3 | 1
| 40 | D/G#4 | Under Excitation | [5 empty] | 0.5 | GCP#4 | 1
207 | 32R | D/G#1 | Reverse Power | [5 empty] | 0.5 | GCP#1 | 1
| 32R | D/G#2 | Reverse Power | [5 empty] | 0.5 | GCP#2 | 1
| 32R | D/G#3 | Reverse Power | [5 empty] | 0.5 | GCP#3 | 1
| 32R | D/G#4 | Reverse Power | [5 empty] | 0.5 | GCP#4 | 1
208 | 81 | D/G#1 | Frequency | [5 empty] | 0.5 | GCP#1 | 1
| 81 | D/G#2 | Frequency | [5 empty] | 0.5 | GCP#2 | 1
| 81 | D/G#3 | Frequency | [5 empty] | 0.5 | GCP#3 | 1
| 81 | D/G#4 | Frequency | [5 empty] | 0.5 | GCP#4 | 1
209 | 46 | D/G#1 | Negative Over Current | [5 empty] | 0.5 | GCP#1 | 1
| 46 | D/G#2 | Negative Over Current | [5 empty] | 0.5 | GCP#2 | 1
| 46 | D/G#3 | Negative Over Current | [5 empty] | 0.5 | GCP#3 | 1
| 46 | D/G#4 | Negative Over Current | [5 empty] | 0.5 | GCP#4 | 1
210 | 86 | D/G#1 | Lockout | [5 empty] | 0.5 | GCP#1 | 1
| 86 | D/G#2 | Lockout | [5 empty] | 0.5 | GCP#2 | 1
| 86 | D/G#3 | Lockout | [5 empty] | 0.5 | GCP#3 | 1
| 86 | D/G#4 | Lockout | [5 empty] | 0.5 | GCP#4 | 1
211 | 50,51 |  | Over Current(LTD,STD,INST) |  |  |  | M4269 | Boolean |  | GCP | 1 |  | Step up feeder
212 | 50,51 |  | Over Current(LTD,STD,INST) |  |  |  | M4270 | Boolean |  | GCP | 1 |  | Step down feeder
213 | 51N |  | Over Current |  |  |  | M4271 | Boolean |  | GCP | 1 |  | NGR
214 | 5E | D/G#1 | Emergency stop local box |  | Digital |  |  |  | 0.5 | Gen Local Box#1 | 1
| 5E | D/G#2 | Emergency stop local box |  | Digital |  |  |  | 0.5 | Gen Local Box#2 | 1
| 5E | D/G#3 | Emergency stop local box |  | Digital |  |  |  | 0.5 | Gen Local Box#3 | 1
| 5E | D/G#4 | Emergency stop local box |  | Digital |  |  |  | 0.5 | Gen Local Box#4 | 1