## Sheet1
Engine | Name | I/O Type | Modbus Address | Data Type (16 bit Int / Boolean?)
D/G#1 | EXH. GAS T/C OUT | Analog | 40001 | 16 bit Int
D/G#1 | MONITORING OF OIL MIST LEVEL | Analog | 40002 | 16 bit Int
D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | Analog | 40003 | 16 bit Int
D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | Analog | 40004 | 16 bit Int
D/G#1 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | Analog | 40005 | 16 bit Int
D/G#1 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | Analog | 40006 | 16 bit Int
D/G#1 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | Analog | 40007 | 16 bit Int
D/G#1 | EXH. GAS No. 1 CYL, OUT | Analog | 40008 | 16 bit Int
D/G#1 | EXH. GAS No. 2 CYL, OUT | Analog | 40009 | 16 bit Int
D/G#1 | EXH. GAS No. 3 CYL, OUT | Analog | 40010 | 16 bit Int
D/G#1 | EXH. GAS No. 4 CYL, OUT | Analog | 40011 | 16 bit Int
D/G#1 | EXH. GAS No. 5 CYL, OUT | Analog | 40012 | 16 bit Int
D/G#1 | EXH. GAS No. 6 CYL, OUT | Analog | 40013 | 16 bit Int
D/G#1 | EXH. GAS T/C IN | Analog | 40014 | 16 bit Int
D/G#1 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | Analog | 40051 40052 | 32 bit Int
D/G#1 | D.O. FLOW METER FOR ENGINE INLET | Analog | 40053 40054 | 32 bit Int
D/G#1 | D.O. FLOW METER FOR ENGINE OUTLET | Analog | 40055 40056 | 32 bit Int
D/G#1 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | Analog | 40057 40058 | 32 bit Int
D/G#1 | H.O. FLOW METER FOR ENGINE INLET | Analog | 40059 40060 | 32 bit Int
D/G#1 | H.O. FLOW METER FOR ENGINE OUTLET | Analog | 40061 40062 | 32 bit Int
D/G#1 | PRESS. SENSOR FOR FUEL OIL | Analog | 40015 | 16 bit Int
D/G#1 | PRESS. SENSOR FOR JACKET WATER | Analog | 40016 | 16 bit Int
D/G#1 | PRESS. SENSOR FOR COOLER WATER | Analog | 40017 | 16 bit Int
D/G#1 | PRESS. SENSOR FOR ENGINE L.O. | Analog | 40018 | 16 bit Int
D/G#1 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | Analog | 40019 | 16 bit Int
D/G#1 | PRESS. SENSOR FOR INTAKE-AIR | Analog | 40020 | 16 bit Int
D/G#1 | TEMP. SENSOR FOR JACKET WATER INLET | Analog | 40021 | 16 bit Int
D/G#1 | TEMP. SENSOR FOR JACKET WATER OUTLET | Analog | 40022 | 16 bit Int
D/G#1 | TEMP. SENSOR FOR COOLER WATER INLET | Analog | 40023 | 16 bit Int
D/G#1 | TEMP. SENSOR FOR COOLER WATER OUTLET | Analog | 40024 | 16 bit Int
D/G#1 | TEMP. SENSOR FOR L.O. COOLER INLET | Analog | 40025 | 16 bit Int
D/G#1 | TEMP. SENSOR FOR L.O. COOLER OUTLET | Analog | 40026 | 16 bit Int
D/G#1 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | Analog | 40027 | 16 bit Int
D/G#1 | TEMP. SENSOR for DO Engine inlet | Analog | 40028 | 16 bit Int
D/G#1 | TEMP. SENSOR for DO Engine outlet | Analog | 40029 | 16 bit Int
D/G#1 | TEMP. SENSOR for HO Engine inlet | Analog | 40030 | 16 bit Int
D/G#1 | TEMP. SENSOR for HO Engine outlet | Analog | 40031 | 16 bit Int
D/G#1 | OMD ANALOG OUTPUT BOARD | Analog | 40032 | 16 bit Int
D/G#1 | Voltage [Generator] | Analog | 40033 | 16 bit Int
D/G#1 | Frequency [Generator] | Analog | 40034 | 16 bit Int
D/G#1 | Power Factor [Generator] | Analog | 40035 | 16 bit Int
D/G#1 | Current [Generator] | Analog | 40036 | 16 bit Int
D/G#1 | Running hours [Generator] | Analog | 40063 40064 | 32 bit Int
D/G#1 | Power [Generator] | Analog | 40038 | 16 bit Int
D/G#1 | Engine RPM | Analog | 40039 | 16 bit Int
D/G#2 | EXH. GAS T/C OUT | Analog | 40101 | 16 bit Int
D/G#2 | MONITORING OF OIL MIST LEVEL | Analog | 40102 | 16 bit Int
D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | Analog | 40103 | 16 bit Int
D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | Analog | 40104 | 16 bit Int
D/G#2 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | Analog | 40105 | 16 bit Int
D/G#2 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | Analog | 40106 | 16 bit Int
D/G#2 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | Analog | 40107 | 16 bit Int
D/G#2 | EXH. GAS No. 1 CYL, OUT | Analog | 40108 | 16 bit Int
D/G#2 | EXH. GAS No. 2 CYL, OUT | Analog | 40109 | 16 bit Int
D/G#2 | EXH. GAS No. 3 CYL, OUT | Analog | 40110 | 16 bit Int
D/G#2 | EXH. GAS No. 4 CYL, OUT | Analog | 40111 | 16 bit Int
D/G#2 | EXH. GAS No. 5 CYL, OUT | Analog | 40112 | 16 bit Int
D/G#2 | EXH. GAS No. 6 CYL, OUT | Analog | 40113 | 16 bit Int
D/G#2 | EXH. GAS T/C IN | Analog | 40114 | 16 bit Int
D/G#2 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | Analog | 40151 40152 | 32 bit Int
D/G#2 | D.O. FLOW METER FOR ENGINE INLET | Analog | 40153 40154 | 32 bit Int
D/G#2 | D.O. FLOW METER FOR ENGINE OUTLET | Analog | 40155 40156 | 32 bit Int
D/G#2 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | Analog | 40157 40158 | 32 bit Int
D/G#2 | H.O. FLOW METER FOR ENGINE INLET | Analog | 40159 40160 | 32 bit Int
D/G#2 | H.O. FLOW METER FOR ENGINE OUTLET | Analog | 40161 40162 | 32 bit Int
D/G#2 | PRESS. SENSOR FOR FUEL OIL | Analog | 40115 | 16 bit Int
D/G#2 | PRESS. SENSOR FOR JACKET WATER | Analog | 40116 | 16 bit Int
D/G#2 | PRESS. SENSOR FOR COOLER WATER | Analog | 40117 | 16 bit Int
D/G#2 | PRESS. SENSOR FOR ENGINE L.O. | Analog | 40118 | 16 bit Int
D/G#2 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | Analog | 40119 | 16 bit Int
D/G#2 | PRESS. SENSOR FOR INTAKE-AIR | Analog | 40120 | 16 bit Int
D/G#2 | TEMP. SENSOR FOR JACKET WATER INLET | Analog | 40121 | 16 bit Int
D/G#2 | TEMP. SENSOR FOR JACKET WATER OUTLET | Analog | 40122 | 16 bit Int
D/G#2 | TEMP. SENSOR FOR COOLER WATER INLET | Analog | 40123 | 16 bit Int
D/G#2 | TEMP. SENSOR FOR COOLER WATER OUTLET | Analog | 40124 | 16 bit Int
D/G#2 | TEMP. SENSOR FOR L.O. COOLER INLET | Analog | 40125 | 16 bit Int
D/G#2 | TEMP. SENSOR FOR L.O. COOLER OUTLET | Analog | 40126 | 16 bit Int
D/G#2 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | Analog | 40127 | 16 bit Int
D/G#2 | TEMP. SENSOR for DO Engine inlet | Analog | 40128 | 16 bit Int
D/G#2 | TEMP. SENSOR for DO Engine outlet | Analog | 40129 | 16 bit Int
D/G#2 | TEMP. SENSOR for HO Engine inlet | Analog | 40130 | 16 bit Int
D/G#2 | TEMP. SENSOR for HO Engine outlet | Analog | 40131 | 16 bit Int
D/G#2 | OMD ANALOG OUTPUT BOARD | Analog | 40132 | 16 bit Int
D/G#2 | Voltage [Generator] | Analog | 40133 | 16 bit Int
D/G#2 | Frequency [Generator] | Analog | 40134 | 16 bit Int
D/G#2 | Power Factor [Generator] | Analog | 40135 | 16 bit Int
D/G#2 | Current [Generator] | Analog | 40136 | 16 bit Int
D/G#2 | Running hours [Generator] | Analog | 40163 40164 | 32 bit Int
D/G#2 | Power [Generator] | Analog | 40138 | 16 bit Int
D/G#2 | Engine RPM | Analog | 40139 | 16 bit Int
D/G#3 | EXH. GAS T/C OUT | Analog | 40201 | 16 bit Int
D/G#3 | MONITORING OF OIL MIST LEVEL | Analog | 40202 | 16 bit Int
D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | Analog | 40203 | 16 bit Int
D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | Analog | 40204 | 16 bit Int
D/G#3 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | Analog | 40205 | 16 bit Int
D/G#3 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | Analog | 40206 | 16 bit Int
D/G#3 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | Analog | 40207 | 16 bit Int
D/G#3 | EXH. GAS No. 1 CYL, OUT | Analog | 40208 | 16 bit Int
D/G#3 | EXH. GAS No. 2 CYL, OUT | Analog | 40209 | 16 bit Int
D/G#3 | EXH. GAS No. 3 CYL, OUT | Analog | 40210 | 16 bit Int
D/G#3 | EXH. GAS No. 4 CYL, OUT | Analog | 40211 | 16 bit Int
D/G#3 | EXH. GAS No. 5 CYL, OUT | Analog | 40212 | 16 bit Int
D/G#3 | EXH. GAS No. 6 CYL, OUT | Analog | 40213 | 16 bit Int
D/G#3 | EXH. GAS T/C IN | Analog | 40214 | 16 bit Int
D/G#3 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | Analog | 40251 40252 | 32 bit Int
D/G#3 | D.O. FLOW METER FOR ENGINE INLET | Analog | 40253 40254 | 32 bit Int
D/G#3 | D.O. FLOW METER FOR ENGINE OUTLET | Analog | 40255 40256 | 32 bit Int
D/G#3 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | Analog | 40257 40258 | 32 bit Int
D/G#3 | H.O. FLOW METER FOR ENGINE INLET | Analog | 40259 40260 | 32 bit Int
D/G#3 | H.O. FLOW METER FOR ENGINE OUTLET | Analog | 40261 40262 | 32 bit Int
D/G#3 | PRESS. SENSOR FOR FUEL OIL | Analog | 40215 | 16 bit Int
D/G#3 | PRESS. SENSOR FOR JACKET WATER | Analog | 40216 | 16 bit Int
D/G#3 | PRESS. SENSOR FOR COOLER WATER | Analog | 40217 | 16 bit Int
D/G#3 | PRESS. SENSOR FOR ENGINE L.O. | Analog | 40218 | 16 bit Int
D/G#3 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | Analog | 40219 | 16 bit Int
D/G#3 | PRESS. SENSOR FOR INTAKE-AIR | Analog | 40220 | 16 bit Int
D/G#3 | TEMP. SENSOR FOR JACKET WATER INLET | Analog | 40221 | 16 bit Int
D/G#3 | TEMP. SENSOR FOR JACKET WATER OUTLET | Analog | 40222 | 16 bit Int
D/G#3 | TEMP. SENSOR FOR COOLER WATER INLET | Analog | 40223 | 16 bit Int
D/G#3 | TEMP. SENSOR FOR COOLER WATER OUTLET | Analog | 40224 | 16 bit Int
D/G#3 | TEMP. SENSOR FOR L.O. COOLER INLET | Analog | 40225 | 16 bit Int
D/G#3 | TEMP. SENSOR FOR L.O. COOLER OUTLET | Analog | 40226 | 16 bit Int
D/G#3 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | Analog | 40227 | 16 bit Int
D/G#3 | TEMP. SENSOR for DO Engine inlet | Analog | 40228 | 16 bit Int
D/G#3 | TEMP. SENSOR for DO Engine outlet | Analog | 40229 | 16 bit Int
D/G#3 | TEMP. SENSOR for HO Engine inlet | Analog | 40230 | 16 bit Int
D/G#3 | TEMP. SENSOR for HO Engine outlet | Analog | 40231 | 16 bit Int
D/G#3 | OMD ANALOG OUTPUT BOARD | Analog | 40232 | 16 bit Int
D/G#3 | Voltage [Generator] | Analog | 40233 | 16 bit Int
D/G#3 | Frequency [Generator] | Analog | 40234 | 16 bit Int
D/G#3 | Power Factor [Generator] | Analog | 40235 | 16 bit Int
D/G#3 | Current [Generator] | Analog | 40236 | 16 bit Int
D/G#3 | Running hours [Generator] | Analog | 40263 40264 | 32 bit Int
D/G#3 | Power [Generator] | Analog | 40238 | 16 bit Int
D/G#3 | Engine RPM | Analog | 40239 | 16 bit Int
D/G#4 | EXH. GAS T/C OUT | Analog | 40301 | 16 bit Int
D/G#4 | MONITORING OF OIL MIST LEVEL | Analog | 40302 | 16 bit Int
D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | Analog | 40303 | 16 bit Int
D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | Analog | 40304 | 16 bit Int
D/G#4 | GENERATOR STATOR WINDING SEARCH COIL THERMAL SENSOR | Analog | 40305 | 16 bit Int
D/G#4 | GENERATOR BEARING THERMAL SENSOR (FLY-WHEEL SIDE) | Analog | 40306 | 16 bit Int
D/G#4 | GENERATOR BEARING THERMAL SENSOR (ANTI-FLY-WHEEL SIDE) | Analog | 40307 | 16 bit Int
D/G#4 | EXH. GAS No. 1 CYL, OUT | Analog | 40308 | 16 bit Int
D/G#4 | EXH. GAS No. 2 CYL, OUT | Analog | 40309 | 16 bit Int
D/G#4 | EXH. GAS No. 3 CYL, OUT | Analog | 40310 | 16 bit Int
D/G#4 | EXH. GAS No. 4 CYL, OUT | Analog | 40311 | 16 bit Int
D/G#4 | EXH. GAS No. 5 CYL, OUT | Analog | 40312 | 16 bit Int
D/G#4 | EXH. GAS No. 6 CYL, OUT | Analog | 40313 | 16 bit Int
D/G#4 | EXH. GAS T/C IN | Analog | 40314 | 16 bit Int
D/G#4 | D.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SERVICE TANK) | Analog | 40351 40352 | 32 bit Int
D/G#4 | D.O. FLOW METER FOR ENGINE INLET | Analog | 40353 40354 | 32 bit Int
D/G#4 | D.O. FLOW METER FOR ENGINE OUTLET | Analog | 40355 40356 | 32 bit Int
D/G#4 | H.O. FLOW METER FOR TRANSFER LINE(FROM STORAGE TO SETTLING TANK) | Analog | 40357 40358 | 32 bit Int
D/G#4 | H.O. FLOW METER FOR ENGINE INLET | Analog | 40359 40360 | 32 bit Int
D/G#4 | H.O. FLOW METER FOR ENGINE OUTLET | Analog | 40361 40362 | 32 bit Int
D/G#4 | PRESS. SENSOR FOR FUEL OIL | Analog | 40315 | 16 bit Int
D/G#4 | PRESS. SENSOR FOR JACKET WATER | Analog | 40316 | 16 bit Int
D/G#4 | PRESS. SENSOR FOR COOLER WATER | Analog | 40317 | 16 bit Int
D/G#4 | PRESS. SENSOR FOR ENGINE L.O. | Analog | 40318 | 16 bit Int
D/G#4 | PRESS. SENSOR FOR TURBO-CHARGER L.O. | Analog | 40319 | 16 bit Int
D/G#4 | PRESS. SENSOR FOR INTAKE-AIR | Analog | 40320 | 16 bit Int
D/G#4 | TEMP. SENSOR FOR JACKET WATER INLET | Analog | 40321 | 16 bit Int
D/G#4 | TEMP. SENSOR FOR JACKET WATER OUTLET | Analog | 40322 | 16 bit Int
D/G#4 | TEMP. SENSOR FOR COOLER WATER INLET | Analog | 40323 | 16 bit Int
D/G#4 | TEMP. SENSOR FOR COOLER WATER OUTLET | Analog | 40324 | 16 bit Int
D/G#4 | TEMP. SENSOR FOR L.O. COOLER INLET | Analog | 40325 | 16 bit Int
D/G#4 | TEMP. SENSOR FOR L.O. COOLER OUTLET | Analog | 40326 | 16 bit Int
D/G#4 | TEMP. SENSOR FOR COOLER WATER BEFORE L.O. COOLER | Analog | 40327 | 16 bit Int
D/G#4 | TEMP. SENSOR for DO Engine inlet | Analog | 40328 | 16 bit Int
D/G#4 | TEMP. SENSOR for DO Engine outlet | Analog | 40329 | 16 bit Int
D/G#4 | TEMP. SENSOR for HO Engine inlet | Analog | 40330 | 16 bit Int
D/G#4 | TEMP. SENSOR for HO Engine outlet | Analog | 40331 | 16 bit Int
D/G#4 | OMD ANALOG OUTPUT BOARD | Analog | 40332 | 16 bit Int
D/G#4 | Voltage [Generator] | Analog | 40333 | 16 bit Int
D/G#4 | Frequency [Generator] | Analog | 40334 | 16 bit Int
D/G#4 | Power Factor [Generator] | Analog | 40335 | 16 bit Int
D/G#4 | Current [Generator] | Analog | 40336 | 16 bit Int
D/G#4 | Running hours [Generator] | Analog | 40363 40364 | 32 bit Int
D/G#4 | Power [Generator] | Analog | 40338 | 16 bit Int
D/G#4 | Engine RPM | Analog | 40339 | 16 bit Int